## Sheet1
hass-victron 0.1.7 mapping entities to Modbus register list based on version 3.20 from Victron Energy
Register (hass-victron) | Entity (hass-victron) | Modbus address | dbus-obj-path | Description | writable | Unit | Remarks
gavazi_grid | grid_L1_power: | 2600 | /Ac/L1/Power | Grid L1 - Power | no | W
gavazi_grid | grid_L2_power: | 2601 | /Ac/L2/Power | Grid L2 - Power | no | W
gavazi_grid | grid_L3_power: | 2602 | /Ac/L3/Power | Grid L3 - Power | no | W
gavazi_grid | grid_L1_energy_forward: | 2603 | /Ac/L1/Energy/Forward | Grid L1 - Energy from net | no | kWh
gavazi_grid | grid_L3_energy_forward: | 2605 | /Ac/L3/Energy/Forward | Grid L3 - Energy from net | no | kWh
gavazi_grid | grid_L2_energy_forward: | 2604 | /Ac/L2/Energy/Forward | Grid L2 - Energy from net | no | kWh
gavazi_grid | grid_L1_energy_reverse: | 2606 | /Ac/L1/Energy/Reverse | Grid L1 - Energy to net | no | kWh
gavazi_grid | grid_L2_energy_reverse: | 2607 | /Ac/L2/Energy/Reverse | Grid L2 - Energy to net | no | kWh
gavazi_grid | grid_L3_energy_reverse: | 2608 | /Ac/L3/Energy/Reverse | Grid L3 - Energy to net | no | kWh
gavazi_grid | grid_serial: | 2609 | /Serial | Serial | no |  | The grid meter serial as string (MSB of first register: first character, LSB of last register: last character).
gavazi_grid | grid_L1_voltage: | 2616 | /Ac/L1/Voltage | Grid L1 – Voltage | no | V AC
gavazi_grid | grid_L1_current: | 2617 | /Ac/L1/Current | Grid L1 – Current | no | A AC
gavazi_grid | grid_L2_voltage: | 2618 | /Ac/L2/Voltage | Grid L2 – Voltage | no | V AC
gavazi_grid | grid_L2_current: | 2619 | /Ac/L2/Current | Grid L2 – Current | no | A AC
gavazi_grid | grid_L3_voltage: | 2620 | /Ac/L3/Voltage | Grid L3 – Voltage | no | V AC
gavazi_grid | grid_L3_current: | 2621 | /Ac/L3/Current | Grid L3 – Current | no | A AC
gavazi_grid | grid_L1_energy_forward_total: | 2622 | /Ac/L1/Energy/Forward | Grid L1 - Energy from net | no | kWh
gavazi_grid | grid_L2_energy_forward_total: | 2624 | /Ac/L2/Energy/Forward | Grid L2 - Energy from net | no | kWh
gavazi_grid | grid_L3_energy_forward_total: | 2626 | /Ac/L3/Energy/Forward | Grid L3 - Energy from net | no | kWh
gavazi_grid | grid_L1_energy_reverse_total: | 2628 | /Ac/L1/Energy/Reverse | Grid L1 - Energy to net | no | kWh
gavazi_grid | grid_L2_energy_reverse_total: | 2630 | /Ac/L2/Energy/Reverse | Grid L2 - Energy to net | no | kWh
gavazi_grid | grid_L3_energy_reverse_total: | 2632 | /Ac/L3/Energy/Reverse | Grid L3 - Energy to net | no | kWh
gavazi_grid | grid_energy_forward_total: | 2634 | /Ac/Energy/Forward | Total Energy from net | no | kWh | Depending on the energy summation method used by the meter, this may be different to the sum of the individual counters
gavazi_grid | grid_energy_reverse_total: | 2636 | /Ac/Energy/Reverse | Total Energy to net | no | kWh
vebus | vebus_activein_L1_voltage: | 3 | /Ac/ActiveIn/L1/V | Input voltage phase 1 | no | V AC
vebus | vebus_activein_L2_voltage: | 4 | /Ac/ActiveIn/L2/V | Input voltage phase 2 | no | V AC
vebus | vebus_activein_L3_voltage: | 5 | /Ac/ActiveIn/L3/V | Input voltage phase 3 | no | V AC
vebus | vebus_activein_L1_current: | 6 | /Ac/ActiveIn/L1/I | Input current phase 1 | no | A AC | Positive: current flowing from mains to Multi. Negative: current flowing from Multi to mains.
vebus | vebus_activein_L2_current: | 7 | /Ac/ActiveIn/L2/I | Input current phase 2 | no | A AC | Positive: current flowing from mains to Multi. Negative: current flowing from Multi to mains.
vebus | vebus_activein_L3_current: | 8 | /Ac/ActiveIn/L3/I | Input current phase 3 | no | A AC | Positive: current flowing from mains to Multi. Negative: current flowing from Multi to mains.
vebus | vebus_activein_L1_frequency: | 9 | /Ac/ActiveIn/L1/F | Input frequency 1 | no | Hz
vebus | vebus_activein_L2_frequency: | 10 | /Ac/ActiveIn/L2/F | Input frequency 2 | no | Hz
vebus | vebus_activein_L3_frequency: | 11 | /Ac/ActiveIn/L3/F | Input frequency 3 | no | Hz
vebus | vebus_activein_L1_power: | 12 | /Ac/ActiveIn/L1/P | Input power 1 | no | VA or Watts | Sign meaning equal to Input current
vebus | vebus_activein_L2_power: | 13 | /Ac/ActiveIn/L2/P | Input power 2 | no | VA or Watts | Sign meaning equal to Input current
vebus | vebus_activein_L3_power: | 14 | /Ac/ActiveIn/L3/P | Input power 3 | no | VA or Watts | Sign meaning eaqual to Input current
vebus | vebus_out_L1_voltage: | 15 | /Ac/Out/L1/V | Output voltage phase 1 | no | V AC
vebus | vebus_out_L2_voltage: | 16 | /Ac/Out/L2/V | Output voltage phase 2 | no | V AC
vebus | vebus_out_L3_voltage: | 17 | /Ac/Out/L3/V | Output voltage phase 3 | no | V AC
vebus | vebus_out_L1_current: | 18 | /Ac/Out/L1/I | Output current phase 1 | no | A AC | Postive: current flowing from Multi to the load. Negative: current flowing from load to the Multi.
vebus | vebus_out_L2_current: | 19 | /Ac/Out/L2/I | Output current phase 2 | no | A AC | Postive: current flowing from Multi to the load. Negative: current flowing from load to the Multi.
vebus | vebus_out_L3_current: | 20 | /Ac/Out/L3/I | Output current phase 3 | no | A AC | Postive: current flowing from Multi to the load. Negative: current flowing from load to the Multi.
vebus | vebus_out_L1_frequency: | 21 | /Ac/Out/L1/F | Output frequency | no | Hz
vebus | vebus_activein_currentlimit: | 22 | /Ac/ActiveIn/CurrentLimit | Active input current limit | yes | A | See Venus-OS manual for limitations, for example when VE.Bus BMS or DMC is installed.
vebus | vebus_out_L1_power: | 23 | /Ac/Out/L1/P | Output power 1 | no | VA or Watts | Sign meaning equal to Output current
vebus | vebus_out_L2_power: | 24 | /Ac/Out/L2/P | Output power 2 | no | VA or Watts | Sign meaning equal to Output current
vebus | vebus_out_L3_power: | 25 | /Ac/Out/L3/P | Output power 3 | no | VA or Watts | Sign meaning equal to Output current
vebus | vebus_battery_voltage: | 26 | /Dc/0/Voltage | Battery voltage | no | V DC
vebus | vebus_battery_current: | 27 | /Dc/0/Current | Battery current | no | A DC | Positive: current flowing from the Multi to the dc system. Negative: the other way around.
vebus | vebus_numberofphases: | 28 | /Ac/NumberOfPhases | Phase count | no | count
vebus | vebus_activein_activeinput: | 29 | /Ac/ActiveIn/ActiveInput | Active input | no | 0=AC Input 1;1=AC Input 2;240=Disconnected
vebus | vebus_soc: | 30 | /Soc | VE.Bus state of charge | yes | %
vebus | vebus_state: | 31 | /State | VE.Bus state | no | 0=Off;1=Low Power;2=Fault;3=Bulk;4=Absorption;5=Float;6=Storage;7=Equalize;8=Passthru;9=Inverting;10=Power assist;11=Power supply;244=Sustain;252=External control
vebus | vebus_error: | 32 | /VebusError | VE.Bus Error | no | 0=No error;1=VE.Bus Error 1: Device is switched off because one of the other phases in the system has switched off;2=VE.Bus Error 2: New and old types MK2 are mixed in the system;3=VE.Bus Error 3: Not all- or more than- the expected devices were found in the system;4=VE.Bus Error 4: No other device whatsoever detected;5=VE.Bus Error 5: Overvoltage on AC-out;6=VE.Bus Error 6: Error in DDC Program;7=VE.Bus BMS connected- which requires an Assistant- but no assistant found;10=VE.Bus Error 10: System time synchronisation problem occurred;14=VE.Bus Error 14: Device cannot transmit data;16=VE.Bus Error 16: Dongle missing;17=VE.Bus Error 17: One of the devices assumed master status because the original master failed;18=VE.Bus Error 18: AC Overvoltage on the output of a slave has occurred while already switched off;22=VE.Bus Error 22: This device cannot function as slave;24=VE.Bus Error 24: Switch-over system protection initiated;25=VE.Bus Error 25: Firmware incompatibility. The firmware of one of the connected device is not sufficiently up to date to operate in conjunction with this device;26=VE.Bus Error 26: Internal error
vebus | vebus_mode: | 33 | /Mode | Switch Position | yes | 1=Charger Only;2=Inverter Only;3=On;4=Off | See Venus-OS manual for limitations, for example when VE.Bus BMS or DMC is installed.
vebus | vebus_alarm_hightemperature: | 34 | /Alarms/HighTemperature | Temperature alarm | no | 0=Ok;1=Warning;2=Alarm
vebus | vebus_alarm_lowbattery: | 35 | /Alarms/LowBattery | Low battery alarm | no | 0=Ok;1=Warning;2=Alarm
vebus | vebus_alarm_overload: | 36 | /Alarms/Overload | Overload alarm | no | 0=Ok;1=Warning;2=Alarm
vebus | vebus_L1_acpowersetpoint: | 37 | /Hub4/L1/AcPowerSetpoint | ESS power setpoint phase 1 | yes | W | ESS Mode 3 - Instructs the multi to charge/discharge with giving power. Negative = discharge. Used by the control loop in grid-parallel systems.
vebus | vebus_disablecharge: | 38 | /Hub4/DisableCharge | ESS disable charge flag phase | yes | 0=Charge allowed;1=Charge disabled | ESS Mode 3 - Enables/Disables charge (0=enabled, 1=disabled). Note that power setpoint will yield to this setting
vebus | vebus_disablefeedin: | 39 | /Hub4/DisableFeedIn | ESS disable feedback flag phase | yes | 0=Feed in allowed;1=Feed in disabled | ESS Mode 3 - Enables/Disables feedback (0=enabled, 1=disabled). Note that power setpoint will yield to this setting
vebus | vebus_L2_acpowersetpoint: | 40 | /Hub4/L2/AcPowerSetpoint | ESS power setpoint phase 2 | yes | W | ESS Mode 3 - Instructs the multi to charge/discharge with giving power. Negative = discharge. Used by the control loop in grid-parallel systems.
vebus | vebus_L3_acpowersetpoint: | 41 | /Hub4/L3/AcPowerSetpoint | ESS power setpoint phase 3 | yes | W | ESS Mode 3 - Instructs the multi to charge/discharge with giving power. Negative = discharge. Used by the control loop in grid-parallel systems.
vebus | vebus_alarm_temperaturesensor: | 42 | /Alarms/TemperatureSensor | Temperatur sensor alarm | no | 0=Ok;1=Warning;2=Alarm
vebus | vebus_alarm_voltagesensor: | 43 | /Alarms/VoltageSensor | Voltage sensor alarm | no | 0=Ok;1=Warning;2=Alarm
vebus | vebus_alarm_L1_higtemperature: | 44 | /Alarms/L1/HighTemperature | Temperature alarm L1 | no | 0=Ok;1=Warning;2=Alarm
vebus | vebus_alarm_L1_lowbattery: | 45 | /Alarms/L1/LowBattery | Low battery alarm L1 | no | 0=Ok;1=Warning;2=Alarm
vebus | vebus_alarm_L1_overload: | 46 | /Alarms/L1/Overload | Overload alarm L1 | no | 0=Ok;1=Warning;2=Alarm
vebus | vebus_alarm_L1_ripple: | 47 | /Alarms/L1/Ripple | Ripple alarm L1 | no | 0=Ok;1=Warning;2=Alarm
vebus | vebus_alarm_L2_higtemperature: | 48 | /Alarms/L2/HighTemperature | Temperature alarm L2 | no | 0=Ok;1=Warning;2=Alarm
vebus | vebus_alarm_L2_lowbattery: | 49 | /Alarms/L2/LowBattery | Low battery alarm L2 | no | 0=Ok;1=Warning;2=Alarm
vebus | vebus_alarm_L2_overload: | 50 | /Alarms/L2/Overload | Overload alarm L2 | no | 0=Ok;1=Warning;2=Alarm
vebus | vebus_alarm_L2_ripple: | 51 | /Alarms/L2/Ripple | Ripple alarm L2 | no | 0=Ok;1=Warning;2=Alarm
vebus | vebus_alarm_L3_higtemperature: | 52 | /Alarms/L3/HighTemperature | Temperature alarm L3 | no | 0=Ok;1=Warning;2=Alarm
vebus | vebus_alarm_L3_lowbattery: | 53 | /Alarms/L3/LowBattery | Low battery alarm L3 | no | 0=Ok;1=Warning;2=Alarm
vebus | vebus_alarm_L3_overload: | 54 | /Alarms/L3/Overload | Overload alarm L3 | no | 0=Ok;1=Warning;2=Alarm
vebus | vebus_alarm_L3_ripple: | 55 | /Alarms/L3/Ripple | Ripple alarm L3 | no | 0=Ok;1=Warning;2=Alarm
vebus | vebus_pvinverter_disable: | 56 | /PvInverter/Disable | Disable PV inverter | yes | 0=PV enabled;1=PV disabled | Disable PV inverter on AC out (using frequency shifting). Only works when vebus device is in inverter mode. Needs ESS or PV inverter assistant
vebus | vebus_bms_allowtocharge: | 57 | /Bms/AllowToCharge | VE.Bus BMS allows battery to be charged | no | 0=No;1=Yes | VE.Bus BMS allows the battery to be charged
vebus | vebus_bms_allowtodischarge: | 58 | /Bms/AllowToDischarge | VE.Bus BMS allows battery to be discharged | no | 0=No;1=Yes | VE.Bus BMS allows the battery to be discharged
vebus | vebus_bms_bmsexpected: | 59 | /Bms/BmsExpected | VE.Bus BMS is expected | no | 0=No;1=Yes | Presence of VE.Bus BMS is expected based on vebus settings (presence of ESS or BMS assistant)
vebus | vebus_bms_error: | 60 | /Bms/Error | VE.Bus BMS error | no | 0=No;1=Yes
vebus | vebus_battery_temperature: | 61 | /Dc/0/Temperature | Battery temperature | no | Degrees celsius
vebus | vebus_systemreset: | 62 | /SystemReset | VE.Bus Reset | yes | 1=VE.Bus reset | Any write action will cause a reset
vebus | vebus_alarm_phaserotation: | 63 | /Alarms/PhaseRotation | Phase rotation warning | no | 0=Ok;1=Warning
vebus | vebus_alarm_gridlost: | 64 | /Alarms/GridLost | Grid lost alarm | no | 0=Ok;2=Alarm
vebus | vebus_donotfeedinovervoltage: | 65 | /Hub4/DoNotFeedInOvervoltage | Feed DC overvoltage into grid | yes | 0=Feed in overvoltage;1=Do not feed in overvoltage
vebus | vebus_L1_maxfeedinpower: | 66 | /Hub4/L1/MaxFeedInPower | Maximum overvoltage feed-in power L1 | yes | W
vebus | vebus_L2_maxfeedinpower: | 67 | /Hub4/L2/MaxFeedInPower | Maximum overvoltage feed-in power L2 | yes | W
vebus | vebus_L3_maxfeedinpower: | 68 | /Hub4/L3/MaxFeedInPower | Maximum overvoltage feed-in power L3 | yes | W
vebus | vebus_state_ignoreacin1: | 69 | /Ac/State/IgnoreAcIn1 | AC input 1 ignored | no | 0=AC input not ignored;1=AC input ignored
vebus | vebus_state_ignoreacin2: | 70 | /Ac/State/IgnoreAcIn2 | AC input 2 ignored | no | 0=AC input not ignored;1=AC input ignored
vebus | vebus_targetpowerismaxfeedin: | 71 | /Hub4/TargetPowerIsMaxFeedIn | AcPowerSetpoint acts as feed-in limit | yes | 0=AcPowerSetpoint interpreted normally; 1=AcPowerSetpoint is OvervoltageFeedIn limit | When set to 1, the Multi behaves as if DoNotFeedInOvervoltage is disabled and AcPowerSetpoint is the maximum allowed feed-in
vebus | vebus_fixsolaroffsetto100mv: | 72 | /Hub4/FixSolarOffsetTo100mV | Solar offset voltage | yes | 0=OvervoltageFeedIn uses 1V offset; 1=OvervoltageFeedIn uses 0.1V offset | When feeding overvoltage into the grid, the solar chargers are set to a higher voltage. This flag determines the size of the offset (per 12V increment).
vebus | vebus_sustain: | 73 | /Hub4/Sustain | Sustain active | no | 0=Sustain inactive; 1=Sustain active
vebus | vebus_acin1toacout: | 74 | /Energy/AcIn1ToAcOut | Energy from AC-In 1 to AC-out | no | kWh | PLEASE NOTE:
vebus | vebus_acin1toinverter: | 76 | /Energy/AcIn1ToInverter | Energy from AC-In 1 to battery | no | kWh | Energy counters from the Multi(s) are volatile.
vebus | vebus_acin2toacout: | 78 | /Energy/AcIn2ToAcOut | Energy from AC-In 2 to AC-out | no | kWh | These energy counters reset to zero when the Multi is switched off.
vebus | vebus_acin2toinverter: | 80 | /Energy/AcIn2ToInverter | Energy from AC-In 2 to battery | no | kWh | These energy counters ALSO reset to zero when the GX-device reboots.
vebus | vebus_acouttoacin1: | 82 | /Energy/AcOutToAcIn1 | Energy from AC-out to AC-in 1 (reverse fed PV) | no | kWh
vebus | vebus_acouttoacin2: | 84 | /Energy/AcOutToAcIn2 | Energy from AC-out to AC-in 2 (reverse fed PV) | no | kWh
vebus | vebus_invertertoacin1: | 86 | /Energy/InverterToAcIn1 | Energy from battery to AC-in 1 | no | kWh
vebus | vebus_invertertoacin2: | 88 | /Energy/InverterToAcIn2 | Energy from battery to AC-in 2 | no | kWh
vebus | vebus_invertertoacout: | 90 | /Energy/InverterToAcOut | Energy from battery to AC-out | no | kWh
vebus | vebus_outtoinverter: | 92 | /Energy/OutToInverter | Energy from AC-out to battery (typically from PV-inverter) | no | kWh
battery | battery_voltage: | 259 | /Dc/0/Voltage | Battery voltage | no | V DC
battery | battery_starter_voltage: | 260 | /Dc/1/Voltage | Starter battery voltage | no | V DC
battery | battery_current: | 261 | /Dc/0/Current | Current | no | A DC | Postive: battery begin charged. Negative: battery being discharged
battery | battery_temperature: | 262 | /Dc/0/Temperature | Battery temperature | no | Degrees celsius | In degrees Celsius
battery | battery_midvoltage: | 263 | /Dc/0/MidVoltage | Mid-point voltage of the battery bank | no | V DC
battery | battery_midvoltagedeviation: | 264 | /Dc/0/MidVoltageDeviation | Mid-point deviation of the battery bank | no | %
battery | battery_consumedamphours: | 265 | /ConsumedAmphours | Consumed Amphours | no | Ah | Always negative (to have the same sign as the current).
battery | battery_soc: | 266 | /Soc | State of charge | no | %
battery | battery_alarm: | 267 | /Alarms/Alarm | Alarm | no | 0=No alarm;2=Alarm | 2015-01-19: Deprecated for CCGX. Value is always 0.
battery | battery_alarm_lowvoltage: | 268 | /Alarms/LowVoltage | Low voltage alarm | no | 0=No alarm;2=Alarm
battery | battery_alarm_highvoltage: | 269 | /Alarms/HighVoltage | High voltage alarm | no | 0=No alarm;2=Alarm
battery | battery_alarm_lowstartervoltage: | 270 | /Alarms/LowStarterVoltage | Low starter-voltage alarm | no | 0=No alarm;2=Alarm
battery | battery_alarm_highstartervoltage: | 271 | /Alarms/HighStarterVoltage | High starter-voltage alarm | no | 0=No alarm;2=Alarm
battery | battery_alarm_lowsoc: | 272 | /Alarms/LowSoc | Low State-of-charge alarm | no | 0=No alarm;2=Alarm
battery | battery_alarm_lowtemperature: | 273 | /Alarms/LowTemperature | Low temperature alarm | no | 0=No alarm;2=Alarm
battery | battery_alarm_hightemperature: | 274 | /Alarms/HighTemperature | High temperature alarm | no | 0=No alarm;2=Alarm
battery | battery_alarm_midvoltage: | 275 | /Alarms/MidVoltage | Mid-voltage alarm | no | 0=No alarm;2=Alarm
battery | battery_alarm_lowfusedvoltage: | 276 | /Alarms/LowFusedVoltage | Low fused-voltage alarm | no | 0=No alarm;2=Alarm | 2014-12-13: Deprecated because over-engineered. Value is always 0.
battery | battery_alarm_highfusedvoltage: | 277 | /Alarms/HighFusedVoltage | High fused-voltage alarm | no | 0=No alarm;2=Alarm | 2014-12-13: Deprecated because over-engineered. Value is always 0.
battery | battery_alarm_fuseblown: | 278 | /Alarms/FuseBlown | Fuse blown alarm | no | 0=No alarm;2=Alarm
battery | battery_alarm_highinternaltemperature: | 279 | /Alarms/HighInternalTemperature | High internal-temperature alarm | no | 0=No alarm;2=Alarm
battery | battery_relay: | 280 | /Relay/0/State | Relay status | yes | 0=Open;1=Closed | Not supported by CAN.Bus BMS batteries.
battery | battery_history_deepestdischarge: | 281 | /History/DeepestDischarge | Deepest discharge | no | Ah | Not supported by CAN.Bus BMS batteries.
battery | battery_history_lastdischarge: | 282 | /History/LastDischarge | Last discharge | no | Ah | Not supported by CAN.Bus BMS batteries.
battery | battery_history_averagedischarge: | 283 | /History/AverageDischarge | Average discharge | no | Ah | Not supported by CAN.Bus BMS batteries.
battery | battery_history_chargecycles: | 284 | /History/ChargeCycles | Charge cycles | no | count | Not supported by CAN.Bus BMS batteries.
battery | battery_history_fulldischarges: | 285 | /History/FullDischarges | Full discharges | no | count | Not supported by CAN.Bus BMS batteries.
battery | battery_history_totalahdrawn: | 286 | /History/TotalAhDrawn | Total Ah drawn | no | Ah | Not supported by CAN.Bus BMS batteries.
battery | battery_history_minimumvoltage: | 287 | /History/MinimumVoltage | Minimum voltage | no | V DC | Not supported by CAN.Bus BMS batteries.
battery | battery_history_maximumvoltage: | 288 | /History/MaximumVoltage | Maximum voltage | no | V DC | Not supported by CAN.Bus BMS batteries.
battery | battery_history_timesincelastfullcharge: | 289 | /History/TimeSinceLastFullCharge | Time since last full charge | no | seconds | Not supported by CAN.Bus BMS batteries.
battery | battery_history_automaticsyncs: | 290 | /History/AutomaticSyncs | Automatic syncs | no | count | Not supported by CAN.Bus BMS batteries.
battery | battery_history_lowvoltagealarms: | 291 | /History/LowVoltageAlarms | Low voltage alarms | no | count | Not supported by CAN.Bus BMS batteries.
battery | battery_history_highvoltagealarms: | 292 | /History/HighVoltageAlarms | High voltage alarms | no | count | Not supported by CAN.Bus BMS batteries.
battery | battery_history_lowstartervoltagealarms: | 293 | /History/LowStarterVoltageAlarms | Low starter voltage alarms | no | count | Not supported by CAN.Bus BMS batteries.
battery | battery_history_highstartervoltagealarms: | 294 | /History/HighStarterVoltageAlarms | High starter voltage alarms | no | count | Not supported by CAN.Bus BMS batteries.
battery | battery_history_minimumstartervoltage: | 295 | /History/MinimumStarterVoltage | Minimum starter voltage | no | V DC | Not supported by CAN.Bus BMS batteries.
battery | battery_history_maximumstartervoltage: | 296 | /History/MaximumStarterVoltage | Maximum starter voltage | no | V DC | Not supported by CAN.Bus BMS batteries.
battery | battery_history_lowfusedvoltagealarms: | 297 | /History/LowFusedVoltageAlarms | Low fused-voltage alarms | no | count | 2014-12-13: Deprecated because over-engineered. Value is always 0.
battery | battery_history_highfusedvoltagealarms: | 298 | /History/HighFusedVoltageAlarms | High fused-voltage alarms | no | count | 2014-12-13: Deprecated because over-engineered. Value is always 0.
battery | battery_history_minimumfusedvoltage: | 299 | /History/MinimumFusedVoltage | Minimum fused voltage | no | V DC | 2014-12-13: Deprecated because over-engineered. Value is always 0.
battery | battery_history_maximumfusedvoltage: | 300 | /History/MaximumFusedVoltage | Maximum fused voltage | no | V DC | 2014-12-13: Deprecated because over-engineered. Value is always 0.
battery | battery_history_dischargedenergy: | 301 | /History/DischargedEnergy | Discharged Energy | no | kWh | Not supported by CAN.Bus BMS batteries.
battery | battery_history_chargedenergy: | 302 | /History/ChargedEnergy | Charged Energy | no | kWh | Not supported by CAN.Bus BMS batteries.
battery | battery_timetogo: | 303 | /TimeToGo | Time to go | no | seconds | Special value: 0 = charging. Not supported by CAN.Bus BMS batteries.
battery | battery_soh: | 304 | /Soh | State of health | no | % | Not supported by Victron products. Supported by CAN.Bus batteries.
battery | battery_info_maxchargevoltage: | 305 | /Info/MaxChargeVoltage | Max charge voltage | no | V DC | Not supported by Victron products. Supported by CAN.Bus batteries.
battery | battery_info_batterylowvoltage: | 306 | /Info/BatteryLowVoltage | Min discharge voltage | no | V DC | Not supported by Victron products. Supported by CAN.Bus batteries.
battery | battery_info_maxchargecurrent: | 307 | /Info/MaxChargeCurrent | Max charge current | no | A DC | Not supported by Victron products. Supported by CAN.Bus batteries.
battery | battery_info_maxdischargecurrent: | 308 | /Info/MaxDischargeCurrent | Max discharge current | no | A DC | Not supported by Victron products. Supported by CAN.Bus batteries.
battery | battery_capacity: | 309 | /Capacity | Capacity | no | Ah
battery | battery_diagnostics_lasterror_1_time: | 310 | /Diagnostics/LastErrors/1/Time | Diagnostics; 1st last error timestamp | no
battery | battery_diagnostics_lasterror_2_time: | 312 | /Diagnostics/LastErrors/2/Time | Diagnostics; 2nd last error timestamp | no
battery | battery_diagnostics_lasterror_3_time: | 314 | /Diagnostics/LastErrors/3/Time | Diagnostics; 3rd last error timestamp | no
battery | battery_diagnostics_lasterror_4_time: | 316 | /Diagnostics/LastErrors/4/Time | Diagnostics; 4th last error timestamp | no
battery | battery_system_mincelltemperature: | 318 | /System/MinCellTemperature | Minimum cell temperature | no | Degrees celsius
battery | battery_system_maxcelltemperature: | 319 | /System/MaxCellTemperature | Maximum cell temperature | no | Degrees celsius
battery | battery_alarm_higchargecurrent: | 320 | /Alarms/HighChargeCurrent | High charge current alarm | no | 0=No alarm;2=Alarm
battery | battery_alarm_highdischargecurrent: | 321 | /Alarms/HighDischargeCurrent | High discharge current alarm | no | 0=No alarm;2=Alarm
battery | battery_alarm_cellimbalance: | 322 | /Alarms/CellImbalance | Cell imbalance alarm | no | 0=No alarm;2=Alarm
battery | battery_alarm_internalfailure: | 323 | /Alarms/InternalFailure | Internal failure alarm | no | 0=No alarm;2=Alarm
battery | battery_alarm_highchargetemperature: | 324 | /Alarms/HighChargeTemperature | High charge temperature alarm | no | 0=No alarm;2=Alarm
battery | battery_alarm_lowchargetemperature: | 325 | /Alarms/LowChargeTemperature | Low charge temperature alarm | no | 0=No alarm;2=Alarm
battery | battery_alarm_lowcellvoltage: | 326 | /Alarms/LowCellVoltage | Low cell voltage alarm | no | 0=No alarm;1=Almost discharged;2=Alarm
battery_detail | battery_state: | 1282 | /State | State | no | 0=Initializing (Wait start);1=Initializing (before boot);2=Initializing (Before boot delay);3=Initializing (Wait boot);4=Initializing;5=Initializing (Measure battery voltage);6=Initializing (Calculate battery voltage);7=Initializing (Wait bus voltage);8=Initializing (Wait for lynx shunt);9=Running;10=Error (10);11=Unused (11);12=Shutdown;13=Slave updating;14=Standby;15=Going to run;16=Pre-charging;17=Contactor check
battery_detail | battery_error: | 1283 | /ErrorCode | Error | no | 0=No error;1=Battery initialization error;2=No batteries connected;3=Unknown battery connected;4=Different battery type;5=Number of batteries incorrect;6=Lynx Shunt not found;7=Battery measure error;8=Internal calculation error;9=Batteries in series not ok;10=Number of batteries incorrect;11=Hardware error;12=Watchdog error;13=Over voltage;14=Under voltage;15=Over temperature;16=Under temperature;17=Hardware fault;18=Standby shutdown;19=Pre-charge charge error;20=Safety contactor check error;21=Pre-charge discharge error;22=ADC error;23=Slave error;24=Slave warning;25=Pre-charge error;26=Safety contactor error;27=Over current;28=Slave update failed;29=Slave update unavailable;30=Calibration data lost;31=Settings invalid;32=BMS cable;33=Reference failure;34=Wrong system voltage;35=Pre-charge timeout
battery_detail | battery_system_switch: | 1284 | /SystemSwitch | System-switch | no | 0=Disabled;1=Enabled
battery_detail | battery_balancing: | 1285 | /Balancing | Balancing | no | 0=Inactive;1=Active
battery_detail | battery_system_numberofbatteries: | 1286 | /System/NrOfBatteries | System; number of batteries | no | count
battery_detail | battery_system_batteriesparallel: | 1287 | /System/BatteriesParallel | System; batteries parallel | no | count
battery_detail | battery_system_batteriesseries: | 1288 | /System/BatteriesSeries | System; batteries series | no | count
battery_detail | battery_system_numberofcellsperbattery: | 1289 | /System/NrOfCellsPerBattery | System; number of cells per battery | no | count
battery_detail | battery_system_mincellvoltage: | 1290 | /System/MinCellVoltage | System; minimum cell voltage | no | V DC
battery_detail | battery_system_maxcellvoltage: | 1291 | /System/MaxCellVoltage | System; maximum cell voltage | no | V DC
battery_detail | battery_diagnostics_shutdownsdueerror: | 1292 | /Diagnostics/ShutDownsDueError | Diagnostics; shutdowns due to error | no | count
battery_detail | battery_diagnostics_lasterror_1: | 1293 | /Diagnostics/LastErrors/1/Error | Diagnostics; 1st last error | no | 0=No error;1=Battery initialization error;2=No batteries connected;3=Unknown battery connected;4=Different battery type;5=Number of batteries incorrect;6=Lynx Shunt not found;7=Battery measure error;8=Internal calculation error;9=Batteries in series not ok;10=Number of batteries incorrect;11=Hardware error;12=Watchdog error;13=Over voltage;14=Under voltage;15=Over temperature;16=Under temperature;17=Hardware fault;18=Standby shutdown;19=Pre-charge charge error;20=Safety contactor check error;21=Pre-charge discharge error;22=ADC error;23=Slave error;24=Slave warning;25=Pre-charge error;26=Safety contactor error;27=Over current;28=Slave update failed;29=Slave update unavailable;30=Calibration data lost;31=Settings invalid;32=BMS cable;33=Reference failure;34=Wrong system voltage;35=Pre-charge timeout
battery_detail | battery_diagnostics_lasterror_2: | 1294 | /Diagnostics/LastErrors/2/Error | Diagnostics; 2nd last error | no | 0=No error;1=Battery initialization error;2=No batteries connected;3=Unknown battery connected;4=Different battery type;5=Number of batteries incorrect;6=Lynx Shunt not found;7=Battery measure error;8=Internal calculation error;9=Batteries in series not ok;10=Number of batteries incorrect;11=Hardware error;12=Watchdog error;13=Over voltage;14=Under voltage;15=Over temperature;16=Under temperature;17=Hardware fault;18=Standby shutdown;19=Pre-charge charge error;20=Safety contactor check error;21=Pre-charge discharge error;22=ADC error;23=Slave error;24=Slave warning;25=Pre-charge error;26=Safety contactor error;27=Over current;28=Slave update failed;29=Slave update unavailable;30=Calibration data lost;31=Settings invalid;32=BMS cable;33=Reference failure;34=Wrong system voltage;35=Pre-charge timeout
battery_detail | battery_diagnostics_lasterror_3: | 1295 | /Diagnostics/LastErrors/3/Error | Diagnostics; 3rd last error | no | 0=No error;1=Battery initialization error;2=No batteries connected;3=Unknown battery connected;4=Different battery type;5=Number of batteries incorrect;6=Lynx Shunt not found;7=Battery measure error;8=Internal calculation error;9=Batteries in series not ok;10=Number of batteries incorrect;11=Hardware error;12=Watchdog error;13=Over voltage;14=Under voltage;15=Over temperature;16=Under temperature;17=Hardware fault;18=Standby shutdown;19=Pre-charge charge error;20=Safety contactor check error;21=Pre-charge discharge error;22=ADC error;23=Slave error;24=Slave warning;25=Pre-charge error;26=Safety contactor error;27=Over current;28=Slave update failed;29=Slave update unavailable;30=Calibration data lost;31=Settings invalid;32=BMS cable;33=Reference failure;34=Wrong system voltage;35=Pre-charge timeout
battery_detail | battery_diagnostics_lasterror_4: | 1296 | /Diagnostics/LastErrors/4/Error | Diagnostics; 4th last error | no | 0=No error;1=Battery initialization error;2=No batteries connected;3=Unknown battery connected;4=Different battery type;5=Number of batteries incorrect;6=Lynx Shunt not found;7=Battery measure error;8=Internal calculation error;9=Batteries in series not ok;10=Number of batteries incorrect;11=Hardware error;12=Watchdog error;13=Over voltage;14=Under voltage;15=Over temperature;16=Under temperature;17=Hardware fault;18=Standby shutdown;19=Pre-charge charge error;20=Safety contactor check error;21=Pre-charge discharge error;22=ADC error;23=Slave error;24=Slave warning;25=Pre-charge error;26=Safety contactor error;27=Over current;28=Slave update failed;29=Slave update unavailable;30=Calibration data lost;31=Settings invalid;32=BMS cable;33=Reference failure;34=Wrong system voltage;35=Pre-charge timeout
battery_detail | battery_io_allowtocharge: | 1297 | /Io/AllowToCharge | IO; allow to charge | no | 0=No;1=Yes
battery_detail | battery_io_allowtodischarge: | 1298 | /Io/AllowToDischarge | IO; allow to discharge | no | 0=No;1=Yes
battery_detail | battery_io_externalrelay: | 1299 | /Io/ExternalRelay | IO; external relay | no | 0=Inactive;1=Active
battery_detail | battery_history_minimumcellvoltage: | 1300 | /History/MinimumCellVoltage | History; Min cell-voltage | no | V DC
battery_detail | battery_history_maximumcellvoltage: | 1301 | /History/MaximumCellVoltage | History; Max cell-voltage | no | V DC
battery_detail | battery_system_numberofmodulesoffline: | 1302 | /System/NrOfModulesOffline | System; number of modules offline | no
battery_detail | battery_system_numberofmodulesonline: | 1303 | /System/NrOfModulesOnline | System; number of modules online | no
battery_detail | battery_system_numberofmodulesblockingcharge: | 1304 | /System/NrOfModulesBlockingCharge | System; number of modules blocking charge | no
battery_detail | battery_system_numberofmodulesblockingdischarge: | 1305 | /System/NrOfModulesBlockingDischarge | System; number of modules blocking discharge | no
battery_detail | battery_system_minvoltagecellid: | 1306 | /System/MinVoltageCellId | System; ID of module with lowest cell voltage | no
battery_detail | battery_system_maxvoltagecellid: | 1310 | /System/MaxVoltageCellId | System; ID of module with highest cell voltage | no
battery_detail | battery_system_mintemperaturecellid: | 1314 | /System/MinTemperatureCellId | System; ID of module with lowest cell temperature | no
battery_detail | battery_system_maxtemperaturecellid: | 1318 | /System/MaxTemperatureCellId | System; ID of module with highest cell temperature | no
solarcharger | solarcharger_battery_voltage: | 771 | /Dc/0/Voltage | Battery voltage | no | V DC
solarcharger | solarcharger_battery_current: | 772 | /Dc/0/Current | Battery current | no | A DC
solarcharger | solarcharger_battery_temperature: | 773 | /Dc/0/Temperature | Battery temperature | no | Degrees celsius | VE.Can MPPTs only
solarcharger | solarcharger_mode: | 774 | /Mode | Charger on/off | yes | 1=On;4=Off | VE.Can MPPTs only
solarcharger | solarcharger_state: | 775 | /State | Charge state | no | 0=Off;2=Fault;3=Bulk;4=Absorption;5=Float;6=Storage;7=Equalize;11=Other (Hub-1);252=External control
solarcharger | solarcharger_pv_voltage: | 776 | /Pv/V | PV voltage | no | V DC | Not available if multiple VE.Can chargers are combined
solarcharger | solarcharger_pv_current: | 777 |  | PV current | no | A DC | Calculated from /Yield/Power and /Pv/V
solarcharger | solarcharger_equallization_pending: | 778 | /Equalization/Pending | Equalization pending | no | 0=No;1=Yes;2=Error;3=Unavailable- Unknown
solarcharger | solarcharger_equalization_time_remaining: | 779 | /Equalization/TimeRemaining | Equalization time remaining | no | seconds
solarcharger | solarcharger_relay: | 780 | /Relay/0/State | Relay on the charger | no | 0=Open;1=Closed
solarcharger | solarcharger_alarm: | 781 | /Alarms/Alarm |  | no | 0=No alarm;2=Alarm | Deprecated. Value is always 0
solarcharger | solarcharger_alarm_lowvoltage: | 782 | /Alarms/LowVoltage | Low batt. voltage alarm | no | 0=No alarm;2=Alarm
solarcharger | solarcharger_alarm_highvoltage: | 783 | /Alarms/HighVoltage | High batt. voltage alarm | no | 0=No alarm;2=Alarm
solarcharger | solarcharger_yield_today: | 784 | /History/Daily/0/Yield | Yield today | no | kWh | Today's yield
solarcharger | solarcharger_maxpower_today: | 785 | /History/Daily/0/MaxPower | Maximum charge power today | no | W | Today's maximum power
solarcharger | solarcharger_yield_yesterday: | 786 | /History/Daily/1/Yield | Yield yesterday | no | kWh | Yesterday's yield
solarcharger | solarcharger_maxpower_yesterday: | 787 | /History/Daily/1/MaxPower | Maximum charge power yesterday | no | W | Yesterday's maximum power
solarcharger | solarcharger_errorcode: | 788 | /ErrorCode | Error code | no | 0=No error;1=Battery temperature too high;2=Battery voltage too high;3=Battery temperature sensor miswired (+);4=Battery temperature sensor miswired (-);5=Battery temperature sensor disconnected;6=Battery voltage sense miswired (+);7=Battery voltage sense miswired (-);8=Battery voltage sense disconnected;9=Battery voltage wire losses too high;17=Charger temperature too high;18=Charger over-current;19=Charger current polarity reversed;20=Bulk time limit reached;22=Charger temperature sensor miswired;23=Charger temperature sensor disconnected;34=Input current too high
solarcharger | solarcharger_yield_power: | 789 | /Yield/Power | PV power | no | W
solarcharger | solarcharger_yield_user: | 790 | /Yield/User | User yield | no | kWh | Energy generated by the solarcharger since last user reset
solarcharger | solarcharger_mppoperationmode: | 791 | /MppOperationMode | MPP operation mode | no | 0=Off;1=Voltage/current limited;2=MPPT active;255=Not available
solarcharger_tracker_voltage | solarcharger_tracker_0_voltage: | 3700 | /Pv/0/V | PV voltage for tracker 0 | no | V DC
solarcharger_tracker_voltage | solarcharger_tracker_1_voltage: | 3701 | /Pv/1/V | PV voltage for tracker 1 | no | V DC
solarcharger_tracker_voltage | solarcharger_tracker_2_voltage: | 3702 | /Pv/2/V | PV voltage for tracker 2 | no | V DC
solarcharger_tracker_voltage | solarcharger_tracker_3_voltage: | 3703 | /Pv/3/V | PV voltage for tracker 3 | no | V DC
solarcharger_tracker | solarcharger_tracker_0_yield_today: | 3708 | /History/Daily/0/Pv/0/Yield | Yield today for tracker 0 | no | kWh
solarcharger_tracker | solarcharger_tracker_1_yield_today: | 3709 | /History/Daily/0/Pv/1/Yield | Yield today for tracker 1 | no | kWh
solarcharger_tracker | solarcharger_tracker_2_yield_today: | 3710 | /History/Daily/0/Pv/2/Yield | Yield today for tracker 2 | no | kWh
solarcharger_tracker | solarcharger_tracker_3_yield_today: | 3711 | /History/Daily/0/Pv/3/Yield | Yield today for tracker 3 | no | kWh
solarcharger_tracker | solarcharger_tracker_0_yield_yesterday: | 3712 | /History/Daily/1/Pv/0/Yield | Yield yesterday for tracker 0 | no | kWh
solarcharger_tracker | solarcharger_tracker_1_yield_yesterday: | 3713 | /History/Daily/1/Pv/1/Yield | Yield yesterday for tracker 1 | no | kWh
solarcharger_tracker | solarcharger_tracker_2_yield_yesterday: | 3714 | /History/Daily/1/Pv/2/Yield | Yield yesterday for tracker 2 | no | kWh
solarcharger_tracker | solarcharger_tracker_3_yield_yesterday: | 3715 | /History/Daily/1/Pv/3/Yield | Yield yesterday for tracker 3 | no | kWh
solarcharger_tracker | solarcharger_tracker_0_maxpower_today: | 3716 | /History/Daily/0/Pv/0/MaxPower | Maximum charge power today for tracker 0 | no | W
solarcharger_tracker | solarcharger_tracker_1_maxpower_today: | 3717 | /History/Daily/0/Pv/1/MaxPower | Maximum charge power today for tracker 1 | no | W
solarcharger_tracker | solarcharger_tracker_2_maxpower_today: | 3718 | /History/Daily/0/Pv/2/MaxPower | Maximum charge power today for tracker 2 | no | W
solarcharger_tracker | solarcharger_tracker_3_maxpower_today: | 3719 | /History/Daily/0/Pv/3/MaxPower | Maximum charge power today for tracker 3 | no | W
solarcharger_tracker | solarcharger_tracker_0_maxpower_yesterday: | 3720 | /History/Daily/1/Pv/0/MaxPower | Maximum charge power yesterday tracker 0 | no | W
solarcharger_tracker | solarcharger_tracker_1_maxpower_yesterday: | 3721 | /History/Daily/1/Pv/1/MaxPower | Maximum charge power yesterday tracker 1 | no | W
solarcharger_tracker | solarcharger_tracker_2_maxpower_yesterday: | 3722 | /History/Daily/1/Pv/2/MaxPower | Maximum charge power yesterday tracker 2 | no | W
solarcharger_tracker | solarcharger_tracker_3_maxpower_yesterday: | 3723 | /History/Daily/1/Pv/3/MaxPower | Maximum charge power yesterday tracker 3 | no | W
solarcharger_tracker | solarcharger_tracker_0_pv_power: | 3724 | /Pv/0/P | PV power for tracker 0 | no | W
solarcharger_tracker | solarcharger_tracker_1_pv_power: | 3725 | /Pv/1/P | PV power for tracker 1 | no | W
solarcharger_tracker | solarcharger_tracker_2_pv_power: | 3726 | /Pv/2/P | PV power for tracker 2 | no | W
solarcharger_tracker | solarcharger_tracker_3_pv_power: | 3727 | /Pv/3/P | PV power for tracker 3 | no | W
pvinverter | pvinverter_position: | 1026 | /Position | Position | no | 0=AC input 1;1=AC output;2=AC input 2
pvinverter | pvinverter_L1_voltage: | 1027 | /Ac/L1/Voltage | L1 Voltage | no | V AC
pvinverter | pvinverter_L1_current: | 1028 | /Ac/L1/Current | L1 Current | no | A AC
pvinverter | pvinverter_L1_power: | 1029 | /Ac/L1/Power | L1 Power | no | W
pvinverter | pvinverter_L1_energy_forward: | 1030 | /Ac/L1/Energy/Forward | L1 Energy | no | kWh | Deprecated. Use 1046 instead.
pvinverter | pvinverter_L2_voltage: | 1031 | /Ac/L2/Voltage | L2 Voltage | no | V AC
pvinverter | pvinverter_L2_current: | 1032 | /Ac/L2/Current | L2 Current | no | A AC
pvinverter | pvinverter_L2_power: | 1033 | /Ac/L2/Power | L2 Power | no | W
pvinverter | pvinverter_L2_energy_forward: | 1034 | /Ac/L2/Energy/Forward | L2 Energy | no | kWh | Deprecated. Use 1048 instead.
pvinverter | pvinverter_L3_voltage: | 1035 | /Ac/L3/Voltage | L3 Voltage | no | V AC
pvinverter | pvinverter_L3_current: | 1036 | /Ac/L3/Current | L3 Current | no | A AC
pvinverter | pvinverter_L3_power: | 1037 | /Ac/L3/Power | L3 Power | no | W
pvinverter | pvinverter_L3_energy_forward: | 1038 | /Ac/L3/Energy/Forward | L3 Energy | no | kWh | Deprecated. Use 1050 instead.
pvinverter | pvinverter_serial: | 1039 | /Serial | Serial | no |  | The system serial as string (MSB of first register: first character, LSB of last register: last character).
pvinverter | pvinverter_L1_energy_forward_total: | 1046 | /Ac/L1/Energy/Forward | L1 Energy | no | kWh
pvinverter | pvinverter_L2_energy_forward_total: | 1048 | /Ac/L2/Energy/Forward | L2 Energy | no | kWh
pvinverter | pvinverter_L3_energy_forward_total: | 1050 | /Ac/L3/Energy/Forward | L3 Energy | no | kWh
pvinverter | pvinverter_power_total: | 1052 | /Ac/Power | Total Power | no | W
pvinverter | pvinverter_power_max_capacity: | 1054 | /Ac/MaxPower | Maximum Power Capacity | no | W
pvinverter | pvinverter_powerlimit: | 1056 | /Ac/PowerLimit | Power limit | yes | W | For use in ESS mode 3
motordrive | motordrive_rpm: | 2048 | /Motor/RPM | Motor RPM | no | RPM
motordrive | motordrive_motor_temperature: | 2049 | /Motor/Temperature | Motor temperature | no | Degrees celsius
motordrive | motordrive_voltage: | 2050 | /Dc/0/Voltage | Controller DC Voltage | no | V DC
motordrive | motordrive_current: | 2051 | /Dc/0/Current | Controller DC Current | no | A DC
motordrive | motordrive_power: | 2052 | /Dc/0/Power | Controller DC Power | no | W | Positive = being powered from battery, Negative is charging battery (regeneration)
motordrive | motordrive_controller_temperature: | 2053 | /Controller/Temperature | Controller Temperature | no | Degrees celsius
charger | charger_voltage_output_1: | 2307 | /Dc/0/Voltage | Output 1 - voltage | no | V DC
charger | charger_current_output_1: | 2308 | /Dc/0/Current | Output 1 - current | no | A DC
charger | charger_temperature: | 2309 | /Dc/0/Temperature | Output 1 - temperature | no | Degrees celsius
charger | charger_voltage_output_2: | 2310 | /Dc/1/Voltage | Output 2 - voltage | no | V DC
charger | charger_current_output_2: | 2311 | /Dc/1/Current | Output 2 - current | no | A DC
charger | charger_voltage_output_3: | 2312 | /Dc/2/Voltage | Output 3 - voltage | no | V DC
charger | charger_current_output_3: | 2313 | /Dc/2/Current | Output 3 - current | no | A DC
charger | charger_L1_current: | 2314 | /Ac/In/L1/I | AC Current | no | A AC
charger | charger_L1_power: | 2315 | /Ac/In/L1/P | AC Power | no | W DC
charger | charger_current_limit: | 2316 | /Ac/In/CurrentLimit | AC Current limit | yes | A AC
charger | charger_mode: | 2317 | /Mode | Charger on/off | yes | 0=Off;1=On;2=Error;3=Unavailable- Unknown
charger | charger_state: | 2318 | /State | Charge state | no | 0=Off;1=Low Power Mode;2=Fault;3=Bulk;4=Absorption;5=Float;6=Storage;7=Equalize;8=Passthru;9=Inverting;10=Power assist;11=Power supply mode;252=External control
charger | charger_errorcode: | 2319 | /ErrorCode | Error code | no | 0=No error;1=Battery temperature too high;2=Battery voltage too high;3=Battery temperature sensor miswired (+);4=Battery temperature sensor miswired (-);5=Battery temperature sensor disconnected;6=Battery voltage sense miswired (+);7=Battery voltage sense miswired (-);8=Battery voltage sense disconnected;9=Battery voltage wire losses too high;17=Charger temperature too high;18=Charger over-current;19=Charger current polarity reversed;20=Bulk time limit reached;22=Charger temperature sensor miswired;23=Charger temperature sensor disconnected;34=Input current too high
charger | charger_relay: | 2320 | /Relay/0/State | Relay on the charger | no | 0=Open;1=Closed
charger | charger_alarm_lowvoltage: | 2321 | /Alarms/LowVoltage | Low voltage alarm | no | 0=No alarm;2=Alarm
charger | charger_alarm_highvoltage: | 2322 | /Alarms/HighVoltage | High voltage alarm | no | 0=No alarm;2=Alarm
settings | settings_ess_acpowersetpoint: | 2700 | /Settings/Cgwacs/AcPowerSetPoint | ESS control loop setpoint | yes | W | ESS Mode 2 - Setpoint for the ESS control-loop in the CCGX. The control-loop will increase/decrease the Multi charge/discharge power to get the grid reading to this setpoint
settings | settings_ess_maxchargepercentage: | 2701 | /Settings/Cgwacs/MaxChargePercentage | ESS max charge current (fractional) | yes | % | ESS Mode 2 - Max charge current for ESS control-loop. The control-loop will use this value to limit the multi power setpoint. For DVCC, use 2705 instead.
settings | settings_ess_maxdischargepercentage: | 2702 | /Settings/Cgwacs/MaxDischargePercentage | ESS max discharge current (fractional) | yes | % | ESS Mode 2 - Max discharge current for ESS control-loop. The control-loop will use this value to limit the multi power setpoint. Currently a value < 50% will disable discharge completely. >=50% allows. Consider using 2704 instead.
settings | settings_ess_acpowersetpoint2: | 2703 | /Settings/Cgwacs/AcPowerSetPoint | ESS control loop setpoint | yes | W | ESS Mode 2 – Same as 2700, but with a different scale factor. Meant for values larger than +-32kW.
settings | settings_ess_maxdischargepower: | 2704 | /Settings/Cgwacs/MaxDischargePower | ESS max discharge current | yes | W | ESS Mode 2 – similar to 2702, but as an absolute value instead of a percentage.
settings | settings_ess_maxchargecurrent: | 2705 | /Settings/SystemSetup/MaxChargeCurrent | DVCC system max charge current | yes | A DC | ESS Mode 2 with DVCC – Maximum system charge current. -1 Disables.
settings | settings_ess_maxfeedinpower: | 2706 | /Settings/Cgwacs/MaxFeedInPower | Maximum System Grid Feed In | yes | W | -1: No limit, >=0: limited system feed-in. Applies to DC-coupled and AC-coupled feed-in.
settings | settings_ess_overvoltagefeedin: | 2707 | /Settings/Cgwacs/OvervoltageFeedIn | Feed excess DC-coupled PV into grid | yes | 0=Don’t feed excess DC-tied PV into grid; 1=Feed excess DC-tied PV into the grid | Also known as Overvoltage Feed-in
settings | settings_ess_preventfeedback: | 2708 | /Settings/Cgwacs/PreventFeedback | Don’t feed excess AC-coupled PV into grid | yes | 0=Feed excess AC-tied PV into grid; 1=Don’t feed excess AC-tied PV into the grid | Formerly called Fronius Zero-Feedin
settings | settings_ess_feedinpowerlimit: | 2709 | /PvPowerLimiterActive | Grid limiting status | no | 0=Feed-in limiting is inactive; 1=Feed-in limiting is active | Applies to both AC-coupled and DC-coupled limiting
settings | settings_systemsetup_maxchargevoltage: | 2710 | /Settings/SystemSetup/MaxChargeVoltage | Limit managed battery voltage | yes | V DC | Only used if there is a managed battery in the system
gps | gps_latitude: | 2800 | /Position/Latitude | Latitude | no | Decimal degrees
gps | gps_longitude: | 2802 | /Position/Longitude | Longitude | no | Decimal degrees
gps | gps_course: | 2804 | /Course | Course | no | Degrees | Direction of movement 0-360 degrees
gps | gps_speed: | 2805 | /Speed | Speed | no | m/s | Speed in m/s
gps | gps_fix: | 2806 | /Fix | GPS fix | no |  | 0: no fix, 1: fix
gps | gps_numberofsatellites: | 2807 | /NrOfSatellites | GPS number of satellites | no
gps | gps_altitude: | 2808 | /Altitude | Altitude | no | m
settings_ess | settings_ess_batterylife_state: | 2900 | /Settings/CGwacs/BatteryLife/State | ESS BatteryLife state | yes | 0=Unused, BL disabled;1=Restarting;2=Self-consumption;3=Self-consumption;4=Self-consumption;5=Discharge disabled;6=Force charge;7=Sustain;8=Low Soc Recharge;9=Keep batteries charged;10=BL Disabled;11=BL Disabled (Low SoC);12=BL Disabled (Low SOC recharge) | Use value 0 (disable) and 1(enable) for writing only
settings_ess | settings_ess_batterylife_minimumsoc: | 2901 | /Settings/CGwacs/BatteryLife/MinimumSocLimit | ESS Minimum SoC (unless grid fails) | yes | % | Same as the setting in the GUI
settings_ess | settings_ess_mode: | 2902 | /Settings/Cgwacs/Hub4Mode | ESS Mode | yes | 1=ESS with Phase Compensation;2=ESS without phase compensation;3=Disabled/External Control
settings_ess | settings_ess_batterylife_soclimit: | 2903 | /Settings/Cgwacs/BatteryLife/SocLimit | ESS BatteryLife SoC limit (read only) | no | % | This value is maintained by BatteryLife. The Active SOC limit is the lower of this value, and register 2901. Also see https://www.victronenergy.com/media/pg/Energy_Storage_System/en/controlling-depth-of-discharge.html#UUID-af4a7478-4b75-68ac-cf3c-16c381335d1e
tank | tank_productid: | 3000 | /ProductId | Product ID | no
tank | tank_capacity: | 3001 | /Capacity | Tank capacity | no | m3
tank | tank_fluidtype: | 3003 | /FluidType | Tank fluid type | no | 0=Fuel;1=Fresh water;2=Waste water;3=Live well;4=Oil;5=Black water (sewage);6=Gasoline;7=Diesel;8=LPG;9=LNG;10=Hydraulic oil;11=Raw water
tank | tank_level: | 3004 | /Level | Tank level | no | %
tank | tank_remaining: | 3005 | /Remaining | Tank remaining fluid | no | m3
tank | tank_status: | 3007 | /Status | Tank status | no | 0=OK;1=Disconnected;2=Short circuited;3=Reverse Polarity;4=Unknown
inverter_output | inverter_output_L1_current: | 3100 | /Ac/Out/L1/I | Output current | no | A AC
inverter_output | inverter_output_L1_voltage: | 3101 | /Ac/Out/L1/V | Output voltage | no | V AC
inverter_output | inverter_output_L1_power: | 3102 | /Ac/Out/L1/P | Output power | no | W AC
inverter_battery | inverter_battery_voltage: | 3105 | /Dc/0/Voltage | Battery voltage | no | V DC
inverter_battery | inverter_battery_current: | 3106 | /Dc/0/Current | Battery current | no | A DC
inverter_alarm | inverter_alarm_hightemperature: | 3110 | /Alarms/HighTemperature | High temperature alarm | no | 0=No alarm;1=Warning;2=Alarm
inverter_alarm | inverter_alarm_highbatteryvoltage: | 3111 | /Alarms/HighVoltage | High battery voltage alarm | no | 0=No alarm;1=Warning;2=Alarm
inverter_alarm | inverter_alarm_highacoutvoltage: | 3112 | /Alarms/HighVoltageAcOut | High AC-Out voltage alarm | no | 0=No alarm;1=Warning;2=Alarm
inverter_alarm | inverter_alarm_lowtemperature: | 3113 | /Alarms/LowTemperature | Low temperature alarm | no | 0=No alarm;1=Warning;2=Alarm
inverter_alarm | inverter_alarm_lowbatteryvoltage: | 3114 | /Alarms/LowVoltage | Low battery voltage alarm | no | 0=No alarm;1=Warning;2=Alarm
inverter_alarm | inverter_alarm_lowacoutvoltage: | 3115 | /Alarms/LowVoltageAcOut | Low AC-Out voltage alarm | no | 0=No alarm;1=Warning;2=Alarm
inverter_alarm | inverter_alarm_overload: | 3116 | /Alarms/Overload | Overload alarm | no | 0=No alarm;1=Warning;2=Alarm
inverter_alarm | inverter_alarm_ripple: | 3117 | /Alarms/Ripple | Ripple alarm | no | 0=No alarm;1=Warning;2=Alarm
inverter_info | inverter_info_firmwareversion: | 3125 | /FirmwareVersion | Firmware version | no
inverter_info | inverter_info_mode: | 3126 | /Mode | Inverter on/off/eco | yes | 2=On;4=Off;5=Eco
inverter_info | inverter_info_productid: | 3127 | /ProductId | Inverter model | no
inverter_info | inverter_info_state: | 3128 | /State | Inverter state | no | 0=Off;1=Low power mode (search mode);2=Fault;9=Inverting (on)
inverter_energy | inverter_energy_invertertoacout: | 3130 | /Energy/InverterToAcOut | Energy from battery to AC-out | no | kWh
inverter_energy | inverter_energy_outtoinverter: | 3132 | /Energy/OutToInverter | Energy from AC-out to battery | no | kWh
inverter_energy | inverter_energy_solartoacout: | 3134 | /Energy/SolarToAcOut | Energy from solar to AC-out | no | kWh
inverter_energy | inverter_energy_solartobattery: | 3136 | /Energy/SolarToBattery | Energy from solar to battery | no | kWh
inverter_energy | inverter_pv_voltage_single_tracker: | 3138 | /Pv/V | PV voltage (for single tracker units) | no | V DC
inverter_tracker | inverter_tracker_0_voltage: | 3140 | /Pv/0/V | PV voltage for tracker 0 | no | V DC
inverter_tracker | inverter_tracker_1_voltage: | 3141 | /Pv/1/V | PV voltage for tracker 1 | no | V DC
inverter_tracker | inverter_tracker_2_voltage: | 3142 | /Pv/2/V | PV voltage for tracker 2 | no | V DC
inverter_tracker | inverter_tracker_3_voltage: | 3143 | /Pv/3/V | PV voltage for tracker 3 | no | V DC
inverter_tracker_statistics | inverter_tracker_0_yield_today: | 3148 | /History/Daily/0/Pv/0/Yield | Yield today for today on tracker 0 | no | kWh
inverter_tracker_statistics | inverter_tracker_1_yield_today: | 3149 | /History/Daily/0/Pv/1/Yield | Yield today for today on tracker 1 | no | kWh
inverter_tracker_statistics | inverter_tracker_2_yield_today: | 3150 | /History/Daily/0/Pv/2/Yield | Yield today for today on tracker 2 | no | kWh
inverter_tracker_statistics | inverter_tracker_3_yield_today: | 3151 | /History/Daily/0/Pv/3/Yield | Yield today for today on tracker 3 | no | kWh
inverter_tracker_statistics | inverter_tracker_0_yield_yesterday: | 3152 | /History/Daily/1/Pv/0/Yield | Yield today for yesterday on tracker 0 | no | kWh
inverter_tracker_statistics | inverter_tracker_1_yield_yesterday: | 3153 | /History/Daily/1/Pv/1/Yield | Yield today for yesterday on tracker 1 | no | kWh
inverter_tracker_statistics | inverter_tracker_2_yield_yesterday: | 3154 | /History/Daily/1/Pv/2/Yield | Yield today for yesterday on tracker 2 | no | kWh
inverter_tracker_statistics | inverter_tracker_3_yield_yesterday: | 3155 | /History/Daily/1/Pv/3/Yield | Yield today for yesterday on tracker 3 | no | kWh
inverter_tracker_statistics | inverter_tracker_0_maxpower_today: | 3156 | /History/Daily/0/Pv/0/MaxPower | Maximum power for today on tracker 0 | no | W
inverter_tracker_statistics | inverter_tracker_1_maxpower_today: | 3157 | /History/Daily/0/Pv/1/MaxPower | Maximum power for today on tracker 1 | no | W
inverter_tracker_statistics | inverter_tracker_2_maxpower_today: | 3158 | /History/Daily/0/Pv/2/MaxPower | Maximum power for today on tracker 2 | no | W
inverter_tracker_statistics | inverter_tracker_3_maxpower_today: | 3159 | /History/Daily/0/Pv/3/MaxPower | Maximum power for today on tracker 3 | no | W
inverter_tracker_statistics | inverter_tracker_0_maxpower_yesterday: | 3160 | /History/Daily/1/Pv/0/MaxPower | Maximum power for yesterday on tracker 0 | no | W
inverter_tracker_statistics | inverter_tracker_1_maxpower_yesterday: | 3161 | /History/Daily/1/Pv/1/MaxPower | Maximum power for yesterday on tracker 1 | no | W
inverter_tracker_statistics | inverter_tracker_2_maxpower_yesterday: | 3162 | /History/Daily/1/Pv/2/MaxPower | Maximum power for yesterday on tracker 2 | no | W
inverter_tracker_statistics | inverter_tracker_3_maxpower_yesterday: | 3163 | /History/Daily/1/Pv/3/MaxPower | Maximum power for yesterday on tracker 3 | no | W
inverter_tracker_statistics | inverter_tracker_0_power: | 3164 | /Pv/0/P | PV power for tracker 0 | no | W
inverter_tracker_statistics | inverter_tracker_1_power: | 3165 | /Pv/1/P | PV power for tracker 1 | no | W
inverter_tracker_statistics | inverter_tracker_2_power: | 3166 | /Pv/2/P | PV power for tracker 2 | no | W
inverter_tracker_statistics | inverter_tracker_3_power: | 3167 | /Pv/3/P | PV power for tracker 3 | no | W
inverter_tracker_statistics | inverter_alarm_lowsoc: | 3168 | /Alarms/LowSoc | Low SOC alarm | no | 0=No alarm;1=Warning;2=Alarm
genset | genset_L1_voltage: | 3200 | /Ac/L1/Voltage | Phase 1 voltage | no | V AC
genset | genset_L2_voltage: | 3201 | /Ac/L2/Voltage | Phase 2 voltage | no | V AC
genset | genset_L3_voltage: | 3202 | /Ac/L3/Voltage | Phase 3 voltage | no | V AC
genset | genset_L1_current: | 3203 | /Ac/L1/Current | Phase 1 current | no | A AC
genset | genset_L2_current: | 3204 | /Ac/L2/Current | Phase 2 current | no | A AC
genset | genset_L3_current: | 3205 | /Ac/L3/Current | Phase 3 current | no | A AC
genset | genset_L1_power: | 3206 | /Ac/L1/Power | Phase 1 power | no | W
genset | genset_L2_power: | 3207 | /Ac/L2/Power | Phase 2 power | no | W
genset | genset_L3_power: | 3208 | /Ac/L3/Power | Phase 3 power | no | W
genset | genset_L1_frequency: | 3209 | /Ac/L1/Frequency | Phase 1 frequency | no | Hz
genset | genset_L2_frequency: | 3210 | /Ac/L2/Frequency | Phase 2 frequency | no | Hz
genset | genset_L3_frequency: | 3211 | /Ac/L3/Frequency | Phase 3 frequency | no | Hz
genset | genset_productid: | 3212 | /ProductId | Generator model | no
genset | genset_statuscode: | 3213 | /StatusCode | Status | no | 0=Standby;1=Startup 1;2=Startup 2;3=Startup 3;4=Startup 4;5=Startup 5;6=Startup 6;7=Startup 7;8=Running;9=Stopping;10=Error
genset | genset_errorcode: | 3214 | /ErrorCode | Error | no | 0=No error;1=AC voltage L1 too low;2=AC frequency L1 too low;3=AC current too low;4=AC power too low;5=Emergency stop;6=Servo current too low;7=Oil pressure too low;8=Engine temperature too low;9=Winding temperature too low;10=Exhaust temperature too low;13=Starter current too low;14=Glow current too low;15=Glow current too low;16=Fuel holding magnet current too low;17=Stop solenoid hold coil current too low;18=Stop solenoid pull coil current too low;19=Optional DC out current too low;20=5V output voltage too low;21=Boost output current too low;22=Panel supply current too high;25=Starter battery voltage too low;26=Startup aborted (rotation too low);28=Rotation too low;29=Power contactor current too low;30=AC voltage L2 too low;31=AC frequency L2 too low;32=AC current L2 too low;33=AC power L2 too low;34=AC voltage L3 too low;35=AC frequency L3 too low;36=AC current L3 too low;37=AC power L3 too low;62=Fuel temperature too low;63=Fuel level too low;65=AC voltage L1 too high;66=AC frequency too high;67=AC current too high;68=AC power too high;70=Servo current too high;71=Oil pressure too high;72=Engine temperature too high;73=Winding temperature too high;74=Exhaust temperature too low;77=Starter current too low;78=Glow current too high;79=Glow current too high;80=Fuel holding magnet current too high;81=Stop solenoid hold coil current too high;82=Stop solenoid pull coil current too high;83=Optional DC out current too high;84=5V output voltage too high;85=Boost output current too high;89=Starter battery voltage too high;90=Startup aborted (rotation too high);92=Rotation too high;93=Power contactor current too high;94=AC voltage L2 too high;95=AC frequency L2 too high;96=AC current L2 too high;97=AC power L2 too high;98=AC voltage L3 too high;99=AC frequency L3 too high;100=AC current L3 too high;101=AC power L3 too high;126=Fuel temperature too high;127=Fuel level too high;130=Lost control unit;131=Lost panel;132=Service needed;133=Lost 3-phase module;134=Lost AGT module;135=Synchronization failure;137=Intake airfilter;139=Lost sync. module;140=Load-balance failed;141=Sync-mode deactivated;142=Engine controller;148=Rotating field wrong;149=Fuel level sensor lost;150=Init failed;151=Watchdog;152=Out: winding;153=Out: exhaust;154=Out: Cyl. head;155=Inverter over temperature;156=Inverter overload;157=Inverter communication lost;158=Inverter sync failed;159=CAN communication lost;160=L1 overload;161=L2 overload;162=L3 overload;163=DC overload;164=DC overvoltage;165=Emergency stop;166=No connection
genset | genset_autostart: | 3215 | /AutoStart | Auto start | no | 0=Disabled;1=Enabled
genset | genset_engine_load: | 3216 | /Engine/Load | Engine load | no | %
genset | genset_engine_speed: | 3217 | /Engine/Speed | Engine speed | no | RPM
genset | genset_engine_operatinghours: | 3218 | /Engine/OperatingHours | Engine operating hours | no | s
genset | genset_engine_coolanttemperature: | 3219 | /Engine/CoolantTemperature | Engine coolant temperature | no | Degrees celsius
genset | genset_engine_windingtemperature: | 3220 | /Engine/WindingTemperature | Engine winding temperature | no | Degrees celsius
genset | genset_engine_exhausttemperature: | 3221 | /Engine/ExaustTemperature | Engine exhaust temperature | no | Degrees celsius
genset | genset_startervoltage: | 3222 | /StarterVoltage | Starter voltage | no | V DC
genset | genset_start: | 3223 | /Start | Start generator | yes | 0=Stop;1=Start | This is normally controlled by the start/stop service. In Venus 3.00 and later, use com.victronenergy.generator/ManualStart instead.
temperature | temperature_productid: | 3300 | /ProductId | Product ID | no
temperature | temperature_scale: | 3301 | /Scale | Temperature scale factor | no
temperature | temperature_offset: | 3302 | /Offset | Temperature offset | no
temperature | temperature_type: | 3303 | /TemperatureType | Temperature type | no | 0=Battery;1=Fridge;2=Generic
temperature | temperature_temperature: | 3304 | /Temperature | Temperature | no | Degrees celsius
temperature | temperature_status: | 3305 | /Status | Temperature status | no | 0=OK;1=Disconnected;2=Short circuited;3=Reverse Polarity;4=Unknown
temperature | temperature_humidity: | 3306 | /Humidity | Humidity | no | % | Relative humidity as a percentage. Only available on sensors that has this feature, eg Ruuvi.
temperature | temperature_batteryvoltage: | 3307 | /BatteryVoltage | Sensor battery voltage | no | V | Used by wireless tags that have a battery in the sensor
temperature | temperature_pressure: | 3308 | /Pressure | Atmospheric pressure | no | hPa | Only available on sensors that has this feature, eg Ruuvi.
pulsemeter | pulsemeter_aggregate: | 3400 | /Aggregate | Aggregate (measured value) | no | m3
pulsemeter | pulsemeter_count: | 3402 | /Count | Count (number of pulses on meter) | no
digitalinput | digitalinput_count: | 3420 | /Count | Count | no
digitalinput | digitalinput_state: | 3422 | /State | State | no | 0=Low;1=High;2=Off;3=On;4=No;5=Yes;6=Open;7=Closed;8=Alarm;9=OK;10=Running;11=Stopped
digitalinput | digitalinput_alarm: | 3423 | /Alarm | Alarm | no | 0=No alarm;2=Alarm
digitalinput | digitalinput_type: | 3424 | /Type | Type | no | 2=Door;3=Bilge pump;4=Bilge alarm;5=Burglar alarm;6=Smoke alarm;7=Fire alarm;8=CO2 alarm;9=Generator
generator | generator_manualstart: | 3500 | /ManualStart | Manual Start | yes | 0=Stop generator; 1=Start generator
generator | generator_runningbyconditioncode: | 3501 | /RunningByConditionCode | Condition that started the generator | no | 0=Stopped;1=Manual;2=TestRun;3=LossOfComms;4=Soc;5=AcLoad;6=BatteryCurrent;7=BatteryVoltage;8=InverterTemperatur;9=InverterOverload;10=StopOnAc1
generator | generator_runtime: | 3502 | /Runtime | Runtime in seconds | no | seconds
generator | generator_quiethours: | 3503 | /QuietHours | Quiet hours active | no | 0=Quiet hours inactive; 1=Quiet hours active
generator | generator_runtime_2: | 3504 | /Runtime | Runtime in seconds | no | seconds
generator | generator_state: | 3506 | /State | Generator start/stop state | no | 0=Stopped;1=Running;10=Error
generator | generator_error: | 3507 | /Error | Generator remote error | no | 0=No Error;1=Remote disabled;2=Remote fault | Only used for FisherPanda gensets
generator | generator_alarm_nogeneratoratacin: | 3508 | /Alarms/NoGeneratorAtAcIn | Generator not detected at AC input alarm | no | 0=No alarm;2=Alarm
generator | generator_autostartenabled: | 3509 | /AutoStartEnabled | Auto start enabled/disabled | yes | 0=Autostart disabled; 1=Autostart enabled
meteo | meteo_irradiance: | 3600 | /Irradiance | Solar irradiance | no | W/m^2
meteo | meteo_windspeed: | 3601 | /WindSpeed | Wind speed | no | m/s
meteo | meteo_celltemperature: | 3602 | /CellTemperature | Cell temperature of sensor | no | Degrees celsius
meteo | meteo_externaltemperature: | 3603 | /ExternalTemperature | External temperature | no | Degrees celsius
evcharger_productid | evcharger_productid: | 3800 | /ProductId | Product ID | no
evcharger | evcharger_firmwareversion: | 3802 | /FirmwareVersion | Firmware version | no
evcharger | evcharger_serial: | 3804 | /Serial | Serial | no
evcharger | evcharger_model: | 3810 | /Model | Model | no
evcharger | evcharger_maxcurrent: | 3814 | /MaxCurrent | Maximum charge current | yes | A
evcharger | evcharger_mode: | 3815 | /Mode | Mode | yes | 0=Manual;1=Auto
evcharger | evcharger_energy_forward: | 3816 | /Ac/Energy/Forward | Energy consumed by charger | no | kWh
evcharger | evcharger_L1_power: | 3818 | /Ac/L1/Power | L1 Power | no | W
evcharger | evcharger_L2_power: | 3819 | /Ac/L2/Power | L2 Power | no | W
evcharger | evcharger_L3_power: | 3820 | /Ac/L3/Power | L3 Power | no | W
evcharger | evcharger_total_power: | 3821 | /Ac/Power | Total power | no | W
evcharger | evcharger_chargingtime: | 3822 | /ChargingTime | Charging time | no | seconds
evcharger | evcharger_current: | 3823 | /Current | Charge current | no | A
evcharger | evcharger_status: | 3824 | /Status | Status | no | 0=Disconnected; 1=Connected; 2=Charging; 3=Charged; 4=Waiting for sun; 5=Waiting for RFID; 6=Waiting for start; 7=Low SOC; 8=Ground fault; 9=Welded contacts; 10=CP Input shorted; 11=Residual current detected; 12=Under voltage detected; 13=Overvoltage detected; 14=Overheating detected
evcharger | evcharger_setcurrent: | 3825 | /SetCurrent | Set charge current (manual mode) | yes | A
evcharger | evcharger_startstop: | 3826 | /StartStop | Start/stop charging (manual mode) | yes | 0=Stop;1=Start
evcharger | evcharger_position: | 3827 | /Position | Position | yes | 0=AC input 1;1=AC output;2=AC input 2
acload | acload_L1_power: | 3900 | /Ac/L1/Power | L1 Power | no | W
acload | acload_L2_power: | 3901 | /Ac/L2/Power | L2 Power | no | W
acload | acload_L3_power: | 3902 | /Ac/L3/Power | L3 Power | no | W
acload | acload_serial: | 3903 | /Serial | Serial number | no
acload | acload_L1_voltage: | 3910 | /Ac/L1/Voltage | L1 Voltage | no | V AC
acload | acload_L1_current: | 3911 | /Ac/L1/Current | L1 Current | no | A
acload | acload_L2_voltage: | 3912 | /Ac/L2/Voltage | L2 Voltage | no | V AC
acload | acload_L2_current: | 3913 | /Ac/L2/Current | L2 Current | no | A
acload | acload_L3_voltage: | 3914 | /Ac/L3/Voltage | L3 Voltage | no | V AC
acload | acload_L3_current: | 3915 | /Ac/L3/Current | L3 Current | no | A
acload | acload_L1_energy_forward: | 3916 | /Ac/L1/Energy/Forward | L1 Energy | no | kWh
acload | acload_L2_energy_forward: | 3918 | /Ac/L2/Energy/Forward | L2 Energy | no | kWh
acload | acload_L3_energy_forward: | 3920 | /Ac/L3/Energy/Forward | L3 Energy | no | kWh
fuelcell | fuelcell_battery_voltage: | 4000 | /Dc/0/Voltage | Battery voltage | no | V DC
fuelcell | fuelcell_battery_current: | 4001 | /Dc/0/Current | Battery current | no | A
fuelcell | fuelcell_starter_voltage: | 4002 | /Dc/1/Voltage | Auxiliary voltage | no | V DC
fuelcell | fuelcell_temperature: | 4003 | /Dc/0/Temperature | Temperature | no | Degrees celsius
fuelcell | fuelcell_history_energyout: | 4004 | /History/EnergyOut | Total energy produced | no | kWh
fuelcell | fuelcell_alarm_lowvoltage: | 4006 | /Alarms/LowVoltage | Low voltage alarm | no | 0=Ok;1=Warning;2=Alarm
fuelcell | fuelcell_alarm_highvoltage: | 4007 | /Alarms/HighVoltage | High voltage alarm | no | 0=Ok;1=Warning;2=Alarm
fuelcell | fuelcell_alarm_lowstartervoltage: | 4008 | /Alarms/LowStarterVoltage | Low auxiliary voltage alarm | no | 0=Ok;1=Warning;2=Alarm
fuelcell | fuelcell_alarm_highstartervoltage: | 4009 | /Alarms/HighStarterVoltage | High auxiliary voltage alarm | no | 0=Ok;1=Warning;2=Alarm
fuelcell | fuelcell_alarm_lowtemperature: | 4010 | /Alarms/LowTemperature | Low temperature alarm | no | 0=Ok;1=Warning;2=Alarm
fuelcell | fuelcell_alarm_hightemperature: | 4011 | /Alarms/HighTemperature | High temperature alarm | no | 0=Ok;1=Warning;2=Alarm
alternator | alternator_battery_voltage: | 4100 | /Dc/0/Voltage | Battery voltage | no | V DC
alternator | alternator_battery_current: | 4101 | /Dc/0/Current | Battery current | no | A
alternator | alternator_startervoltage: | 4102 | /Dc/1/Voltage | Auxiliary voltage | no | V DC
alternator | alternator_temperature: | 4103 | /Dc/0/Temperature | Temperature | no | Degrees celsius
alternator | alternator_history_energyout: | 4104 | /History/EnergyOut | Total energy produced | no | kWh
alternator | alternator_alarm_lowvoltage: | 4106 | /Alarms/LowVoltage | Low voltage alarm | no | 0=Ok;1=Warning;2=Alarm
alternator | alternator_alarm_highvoltage: | 4107 | /Alarms/HighVoltage | High voltage alarm | no | 0=Ok;1=Warning;2=Alarm
alternator | alternator_alarm_lowstartervoltage: | 4108 | /Alarms/LowStarterVoltage | Low auxiliary voltage alarm | no | 0=Ok;1=Warning;2=Alarm
alternator | alternator_alarm_highstartervoltage: | 4109 | /Alarms/HighStarterVoltage | High auxiliary voltage alarm | no | 0=Ok;1=Warning;2=Alarm
alternator | alternator_alarm_lowtemperature: | 4110 | /Alarms/LowTemperature | Low temperature alarm | no | 0=Ok;1=Warning;2=Alarm
alternator | alternator_alarm_hightemperature: | 4111 | /Alarms/HighTemperature | High temperature alarm | no | 0=Ok;1=Warning;2=Alarm
alternator | alternator_state: | 4112 | /State | Alternator state | no | 0=Off;2=Fault;3=Bulk;4=Absorption;5=Float;6=Storage;7=Equalize;252=External control
alternator | alternator_errorcode: | 4113 | /ErrorCode | Alternator error code | no | 12=High battery temperature;13=High battery voltage;14=Low battery voltage;15=VBat exceeds $CPB;21=High alternator temperature;22=Alternator overspeed;24=Internal error;41=High field FET temperature;42=Sensor missing;43=Low VAlt;44=High Voltage offset;45=VAlt exceeds $CPB;51-52=Battery disconnect request;53=Battery instance out of range;54=Too many BMSes;55=AEBus fault;56=Too many Victron devices;58-61=Battery requested disconnection;91=BMS lost;92=Forced idle;201=DCDC converter fail;201-207=DCDC error
alternator | alternator_engine_speed: | 4114 | /Engine/Speed | Engine speed | no | RPM
alternator | alternator_alternator_speed: | 4115 | /Speed | Alternator speed | no | RPM
alternator | alternator_fielddrive: | 4116 | /FieldDrive | Percentage field drive | no | %
dcsource | dcsource_battery_voltage: | 4200 | /Dc/0/Voltage | Battery voltage | no | V DC
dcsource | dcsource_battery_current: | 4201 | /Dc/0/Current | Battery current | no | A
dcsource | dcsource_starter_voltage: | 4202 | /Dc/1/Voltage | Auxiliary voltage | no | V DC
dcsource | dcsource_temperature: | 4203 | /Dc/0/Temperature | Temperature | no | Degrees celsius
dcsource | dcsource_history_energyout: | 4204 | /History/EnergyOut | Total energy produced | no | kWh
dcsource | dcsource_alarm_lowvoltage: | 4206 | /Alarms/LowVoltage | Low voltage alarm | no | 0=Ok;1=Warning;2=Alarm
dcsource | dcsource_alarm_highvoltage: | 4207 | /Alarms/HighVoltage | High voltage alarm | no | 0=Ok;1=Warning;2=Alarm
dcsource | dcsource_alarm_lowstartervoltage: | 4208 | /Alarms/LowStarterVoltage | Low auxiliary voltage alarm | no | 0=Ok;1=Warning;2=Alarm
dcsource | dcsource_alarm_highstartervoltage: | 4209 | /Alarms/HighStarterVoltage | High auxiliary voltage alarm | no | 0=Ok;1=Warning;2=Alarm
dcsource | dcsource_alarm_lowtemperature: | 4210 | /Alarms/LowTemperature | Low temperature alarm | no | 0=Ok;1=Warning;2=Alarm
dcsource | dcsource_alarm_hightemperature: | 4211 | /Alarms/HighTemperature | High temperature alarm | no | 0=Ok;1=Warning;2=Alarm
dcload | dcload_battery_voltage: | 4300 | /Dc/0/Voltage | Battery voltage | no | V DC
dcload | dcload_battery_current: | 4301 | /Dc/0/Current | Battery current | no | A
dcload | dcload_starter_voltage: | 4302 | /Dc/1/Voltage | Auxiliary voltage | no | V DC
dcload | dcload_temperature: | 4303 | /Dc/0/Temperature | Temperature | no | Degrees celsius
dcload | dcload_history_energyin: | 4304 | /History/EnergyIn | Total energy consumed | no | kWh
dcload | dcload_alarm_lowvoltage: | 4306 | /Alarms/LowVoltage | Low voltage alarm | no | 0=Ok;1=Warning;2=Alarm
dcload | dcload_alarm_highvoltage: | 4307 | /Alarms/HighVoltage | High voltage alarm | no | 0=Ok;1=Warning;2=Alarm
dcload | dcload_alarm_lowstartervoltage: | 4308 | /Alarms/LowStarterVoltage | Low auxiliary voltage alarm | no | 0=Ok;1=Warning;2=Alarm
dcload | dcload_alarm_highstartervoltage: | 4309 | /Alarms/HighStarterVoltage | High auxiliary voltage alarm | no | 0=Ok;1=Warning;2=Alarm
dcload | dcload_alarm_lowtemperature: | 4310 | /Alarms/LowTemperature | Low temperature alarm | no | 0=Ok;1=Warning;2=Alarm
dcload | dcload_alarm_hightemperature: | 4311 | /Alarms/HighTemperature | High temperature alarm | no | 0=Ok;1=Warning;2=Alarm
dcsystem | dcsystem_battery_voltage: | 4400 | /Dc/0/Voltage | Battery voltage | no | V DC
dcsystem | dcsystem_battery_current: | 4401 | /Dc/0/Current | Battery current | no | A
dcsystem | dcsystem_starter_voltage: | 4402 | /Dc/1/Voltage | Auxiliary voltage | no | V DC
dcsystem | dcsystem_temperature: | 4403 | /Dc/0/Temperature | Temperature | no | Degrees celsius
dcsystem | dcsystem_history_energyout: | 4404 | /History/EnergyOut | Total energy produced | no | kWh
dcsystem | dcsystem_history_energyin: | 4406 | /History/EnergyIn | Total energy consumed | no | kWh
dcsystem | dcsystem_alarm_lowvoltage: | 4408 | /Alarms/LowVoltage | Low voltage alarm | no | 0=No alarm;1=Warning; 2=Alarm
dcsystem | dcsystem_alarm_highvoltage: | 4409 | /Alarms/HighVoltage | High voltage alarm | no | 0=No alarm;1=Warning; 2=Alarm
dcsystem | dcsystem_alarm_lowstartervoltage: | 4410 | /Alarms/LowStarterVoltage | Low auxiliary voltage alarm | no | 0=Ok;1=Warning;2=Alarm
dcsystem | dcsystem_alarm_highstartervoltage: | 4411 | /Alarms/HighStarterVoltage | High auxiliary voltage alarm | no | 0=Ok;1=Warning;2=Alarm
dcsystem | dcsystem_alarm_lowtemperature: | 4412 | /Alarms/LowTemperature | Low temperature alarm | no | 0=Ok;1=Warning;2=Alarm
dcsystem | dcsystem_alarm_hightemperature: | 4413 | /Alarms/HighTemperature | High temperature alarm | no | 0=Ok;1=Warning;2=Alarm
multi | multi_input_L1_voltage: | 4500 | /Ac/In/1/L1/V | Input voltage phase 1 | no | V AC
multi | multi_input_L2_voltage: | 4501 | /Ac/In/1/L2/V | Input voltage phase 2 | no | V AC
multi | multi_input_L3_voltage: | 4502 | /Ac/In/1/L3/V | Input voltage phase 3 | no | V AC
multi | multi_input_L1_current: | 4503 | /Ac/In/1/L1/I | Input current phase 1 | no | A AC
multi | multi_input_L2_current: | 4504 | /Ac/In/1/L2/I | Input current phase 2 | no | A AC
multi | multi_input_L3_current: | 4505 | /Ac/In/1/L3/I | Input current phase 3 | no | A AC
multi | multi_input_L1_power: | 4506 | /Ac/In/1/L1/P | Input power phase 1 | no | W
multi | multi_input_L2_power: | 4507 | /Ac/In/1/L2/P | Input power phase 2 | no | W
multi | multi_input_L3_power: | 4508 | /Ac/In/1/L3/P | Input power phase 3 | no | W
multi | multi_input_L1_frequency: | 4509 | /Ac/In/1/L1/F | Input frequency | no | Hz
multi | multi_output_L1_voltage: | 4510 | /Ac/Out/L1/V | Output voltage phase 1 | no | V AC
multi | multi_output_L2_voltage: | 4511 | /Ac/Out/L2/V | Output voltage phase 2 | no | V AC
multi | multi_output_L3_voltage: | 4512 | /Ac/Out/L3/V | Output voltage phase 3 | no | V AC
multi | multi_output_L1_current: | 4513 | /Ac/Out/L1/I | Output current phase 1 | no | A AC
multi | multi_output_L2_current: | 4514 | /Ac/Out/L2/I | Output current phase 2 | no | A AC
multi | multi_output_L3_current: | 4515 | /Ac/Out/L3/I | Output current phase 3 | no | A AC
multi | multi_output_L1_power: | 4516 | /Ac/Out/L1/P | Output power phase 1 | no | W
multi | multi_output_L2_power: | 4517 | /Ac/Out/L2/P | Output power phase 2 | no | W
multi | multi_output_L3_power: | 4518 | /Ac/Out/L3/P | Output power phase 3 | no | W
multi | multi_output_L1_frequency: | 4519 | /Ac/Out/L1/F | Output frequency | no | Hz
multi | multi_input_1_type: | 4520 | /Ac/In/1/Type | AC input 1 source type | no | 0=Unused;1=Grid;2=Genset;3=Shore
multi | multi_input_2_type: | 4521 | /Ac/In/2/Type | AC input 2 source type | no | 0=Unused;1=Grid;2=Genset;3=Shore
multi | multi_input_1_currentlimit: | 4522 | /Ac/In/1/CurrentLimit | Ac input 1 current limit | yes | A
multi | multi_input_2_currentlimit: | 4523 | /Ac/In/2/CurrentLimit | Ac input 2 current limit | yes | A
multi | multi_numberofphases: | 4524 | /Ac/NumberOfPhases | Phase count | no | count
multi | multi_activein_activeinput: | 4525 | /Ac/ActiveIn/ActiveInput | Active AC input | no | 0=AC Input 1;1=AC Input 2;240=Disconnected
multi | multi_battery_voltage: | 4526 | /Dc/0/Voltage | Battery voltage | no | V DC
multi | multi_battery_current: | 4527 | /Dc/0/Current | Battery current | no | A DC
multi | multi_battery_temperature: | 4528 | /Dc/0/Temperature | Battery temperature | no | Degrees celsius
multi | multi_battery_soc: | 4529 | /Soc | Battery State of Charge | no | %
multi | multi_state: | 4530 | /State | Inverter/Charger state | no | 0=Off;1=Low Power;2=Fault;3=Bulk;4=Absorption;5=Float;6=Storage;7=Equalize;8=Passthru;9=Inverting;10=Power assist;11=Power supply;252=External control
multi | multi_mode: | 4531 | /Mode | Switch position | yes | 1=Charger Only;2=Inverter Only;3=On;4=Off
multi | multi_alarm_hightemperature: | 4532 | /Alarms/HighTemperature | Temperature alarm | no | 0=Ok;1=Warning;2=Alarm
multi | multi_alarm_highvoltage: | 4533 | /Alarms/HighVoltage | High voltage alarm | no | 0=Ok;1=Warning;2=Alarm
multi | multi_alarm_highvoltageacout: | 4534 | /Alarms/HighVoltageAcOut | High AC-Out voltage alarm | no | 0=Ok;1=Warning;2=Alarm
multi | multi_alarm_lowtemperature: | 4535 | /Alarms/LowTemperature | Low battery temperature alarm | no | 0=Ok;1=Warning;2=Alarm
multi | multi_alarm_lowvoltage: | 4536 | /Alarms/LowVoltage | Low voltage alarm | no | 0=Ok;1=Warning;2=Alarm
multi | multi_alarm_lowvoltageacout: | 4537 | /Alarms/LowVoltageAcOut | Low AC-Out voltage alarm | no | 0=Ok;1=Warning;2=Alarm
multi | multi_alarm_overload: | 4538 | /Alarms/Overload | Overload alarm | no | 0=Ok;1=Warning;2=Alarm
multi | multi_alarm_ripple: | 4539 | /Alarms/Ripple | High DC ripple alarm | no | 0=Ok;1=Warning;2=Alarm
multi | multi_yield_pv_power: | 4540 | /Yield/Power | PV power | no | W
multi | multi_yield_user: | 4541 | /Yield/User | User yield | no | kWh
multi | multi_relay: | 4542 | /Relay/0/State | Relay on the Multi RS | no | 0=Open;1=Closed
multi | multi_mppoperationmode: | 4543 | /MppOperationMode | MPP operation mode | no | 0=Off;1=Voltage/current limited;2=MPPT active;255=Not available
multi | multi_pv_voltage: | 4544 | /Pv/V | PV voltage | no | V DC
multi | multi_errorcode: | 4545 | /ErrorCode | Error code | no | 0=No error;1=Battery temperature too high;2=Battery voltage too high;3=Battery temperature sensor miswired (+);4=Battery temperature sensor miswired (-);5=Battery temperature sensor disconnected;6=Battery voltage sense miswired (+);7=Battery voltage sense miswired (-);8=Battery voltage sense disconnected;9=Battery voltage wire losses too high;17=Charger temperature too high;18=Charger over-current;19=Charger current polarity reversed;20=Bulk time limit reached;22=Charger temperature sensor miswired;23=Charger temperature sensor disconnected;34=Input current too high
multi | multi_energy_acin1toacout: | 4546 | /Energy/AcIn1ToAcOut | Energy from AC-in-1 to AC-out | no | kWh
multi | multi_energy_acin1toinverter: | 4548 | /Energy/AcIn1ToInverter | Energy from AC-in-1 to battery | no | kWh
multi | multi_energy_acin2toacout: | 4550 | /Energy/AcIn2ToAcOut | Energy from AC-in-2 to AC-out | no | kWh
multi | multi_energy_acin2toinverter: | 4552 | /Energy/AcIn2ToInverter | Energy from AC-in-2 to battery | no | kWh
multi | multi_energy_acouttoacin1: | 4554 | /Energy/AcOutToAcIn1 | Energy from AC-out to AC-in-1 | no | kWh
multi | multi_energy_acouttoacin2: | 4556 | /Energy/AcOutToAcIn2 | Energy from AC-out to AC-in-2 | no | kWh
multi | multi_energy_invertertoacin1: | 4558 | /Energy/InverterToAcIn1 | Energy from battery to AC-in-1 | no | kWh
multi | multi_energy_invertertoacin2: | 4560 | /Energy/InverterToAcIn2 | Energy from battery to AC-in-2 | no | kWh
multi | multi_energy_invertertoacout: | 4562 | /Energy/InverterToAcOut | Energy from battery to AC-out | no | kWh
multi | multi_energy_outtoinverter: | 4564 | /Energy/OutToInverter | Energy from AC-out to battery | no | kWh
multi | multi_energy_solartoacin1: | 4566 | /Energy/SolarToAcIn1 | Energy from solar to AC-in-1 | no | kWh
multi | multi_energy_solartoacin2: | 4568 | /Energy/SolarToAcIn2 | Energy from solar to AC-in-2 | no | kWh
multi | multi_energy_solartoacout: | 4570 | /Energy/SolarToAcOut | Energy from solar to AC-out | no | kWh
multi | mutli_energy_solartobattery: | 4572 | /Energy/SolarToBattery | Energy from solar to battery | no | kWh
multi | multi_history_yield_today: | 4574 | /History/Daily/0/Yield | Yield today | no | kWh
multi | multi_history_maxpower_today: | 4575 | /History/Daily/0/MaxPower | Maximum charge power today | no | W
multi | multi_history_yield_yesterday: | 4576 | /History/Daily/1/Yield | Yield yesterday | no | kWh
multi | multi_history_maxpower_yesterday: | 4577 | /History/Daily/1/MaxPower | Maximum charge power yesterday | no | W
multi | multi_history_tracker_0_yield_today: | 4578 | /History/Daily/0/Pv/0/Yield | Yield today for tracker 0 | no | kWh
multi | multi_history_tracker_1_yield_today: | 4579 | /History/Daily/0/Pv/1/Yield | Yield today for tracker 1 | no | kWh
multi | multi_history_tracker_2_yield_today: | 4580 | /History/Daily/0/Pv/2/Yield | Yield today for tracker 2 | no | kWh
multi | multi_history_tracker_3_yield_today: | 4581 | /History/Daily/0/Pv/3/Yield | Yield today for tracker 3 | no | kWh
multi | multi_history_tracker_0_yield_yesterday: | 4582 | /History/Daily/1/Pv/0/Yield | Yield yesterday for tracker 0 | no | kWh
multi | multi_history_tracker_1_yield_yesterday: | 4583 | /History/Daily/1/Pv/1/Yield | Yield yesterday for tracker 1 | no | kWh
multi | multi_history_tracker_2_yield_yesterday: | 4584 | /History/Daily/1/Pv/2/Yield | Yield yesterday for tracker 2 | no | kWh
multi | multi_history_tracker_3_yield_yesterday: | 4585 | /History/Daily/1/Pv/3/Yield | Yield yesterday for tracker 3 | no | kWh
multi | multi_history_tracker_0_maxpower_today: | 4586 | /History/Daily/0/Pv/0/MaxPower | Maximum charge power today for tracker 0 | no | W
multi | multi_history_tracker_1_maxpower_today: | 4587 | /History/Daily/0/Pv/1/MaxPower | Maximum charge power today for tracker 1 | no | W
multi | multi_history_tracker_2_maxpower_today: | 4588 | /History/Daily/0/Pv/2/MaxPower | Maximum charge power today for tracker 2 | no | W
multi | multi_history_tracker_3_maxpower_today: | 4589 | /History/Daily/0/Pv/3/MaxPower | Maximum charge power today for tracker 3 | no | W
multi | multi_history_tracker_0_maxpower_yesterday: | 4590 | /History/Daily/1/Pv/0/MaxPower | Maximum charge power yesterday tracker 0 | no | W
multi | multi_history_tracker_1_maxpower_yesterday: | 4591 | /History/Daily/1/Pv/1/MaxPower | Maximum charge power yesterday tracker 1 | no | W
multi | multi_history_tracker_2_maxpower_yesterday: | 4592 | /History/Daily/1/Pv/2/MaxPower | Maximum charge power yesterday tracker 2 | no | W
multi | multi_history_tracker_3_maxpower_yesterday: | 4593 | /History/Daily/1/Pv/3/MaxPower | Maximum charge power yesterday tracker 3 | no | W
multi | multi_tracker_0_voltage: | 4594 | /Pv/0/V | PV voltage for tracker 0 | no | V DC
multi | multi_tracker_1_voltage: | 4595 | /Pv/1/V | PV voltage for tracker 1 | no | V DC
multi | multi_tracker_2_voltage: | 4596 | /Pv/2/V | PV voltage for tracker 2 | no | V DC
multi | multi_tracker_3_voltage: | 4597 | /Pv/3/V | PV voltage for tracker 3 | no | V DC
multi | multi_tracker_0_power: | 4598 | /Pv/0/P | PV power for tracker 0 | no | W
multi | multi_tracker_1_power: | 4599 | /Pv/1/P | PV power for tracker 1 | no | W
multi | multi_tracker_2_power: | 4600 | /Pv/2/P | PV power for tracker 2 | no | W
multi | multi_tracker_3_power: | 4601 | /Pv/3/P | PV power for tracker 3 | no | W
multi | multi_alarm_lowsoc: | 4602 | /Alarms/LowSoc | Low SOC alarm | no | 0=No alarm;1=Warning;2=Alarm
system | system_serial: | 800 | /Serial | Serial (System) | no |  | System value -> MAC address of CCGX (represented as string)
system | system_relay_0: | 806 | /Relay/0/State | CCGX Relay 1 state | yes | 0=Open;1=Closed
system | system_relay_1: | 807 | /Relay/1/State | CCGX Relay 2 state | yes | 0=Open;1=Closed | Relay 1 is available on Venus GX only.
system | system_pvonoutput_L1: | 808 | /Ac/PvOnOutput/L1/Power | PV - AC-coupled on output L1 | no | W | Summation of all AC-Coupled PV Inverters on the output
system | system_pvonoutput_L2: | 809 | /Ac/PvOnOutput/L2/Power | PV - AC-coupled on output L2 | no | W
system | system_pvonoutput_L3: | 810 | /Ac/PvOnOutput/L3/Power | PV - AC-coupled on output L3 | no | W
system | system_pvongrid_L1: | 811 | /Ac/PvOnGrid/L1/Power | PV - AC-coupled on input L1 | no | W | Summation of all AC-Coupled PV Inverters on the input
system | system_pvongrid_L2: | 812 | /Ac/PvOnGrid/L2/Power | PV - AC-coupled on input L2 | no | W
system | system_pvongrid_L3: | 813 | /Ac/PvOnGrid/L3/Power | PV - AC-coupled on input L3 | no | W
system | system_pvongenset_L1: | 814 | /Ac/PvOnGenset/L1/Power | PV - AC-coupled on generator L1 | no | W | Summation of all AC-Coupled PV Inverters on a generator. Bit theoretic; this will never be used.
system | system_pvongenset_L2: | 815 | /Ac/PvOnGenset/L2/Power | PV - AC-coupled on generator L2 | no | W
system | system_pvongenset_L3: | 816 | /Ac/PvOnGenset/L3/Power | PV - AC-coupled on generator L3 | no | W
system | system_consumption_L1: | 817 | /Ac/Consumption/L1/Power | AC Consumption L1 | no | W | Power supplied by system to loads.
system | system_consumption_L2: | 818 | /Ac/Consumption/L2/Power | AC Consumption L2 | no | W
system | system_consumption_L3: | 819 | /Ac/Consumption/L3/Power | AC Consumption L3 | no | W
system | system_grid_L1: | 820 | /Ac/Grid/L1/Power | Grid L1 | no | W | Power supplied by Grid to system.
system | system_grid_L2: | 821 | /Ac/Grid/L2/Power | Grid L2 | no | W
system | system_grid_L3: | 822 | /Ac/Grid/L3/Power | Grid L3 | no | W
system | system_genset_L1: | 823 | /Ac/Genset/L1/Power | Genset L1 | no | W | Power supplied by Genset tot system.
system | system_genset_L2: | 824 | /Ac/Genset/L2/Power | Genset L2 | no | W
system | system_genset_L3: | 825 | /Ac/Genset/L3/Power | Genset L3 | no | W
system | system_input_source: | 826 | /Ac/ActiveIn/Source | Active input source | no | 0=Unknown;1=Grid;2=Generator;3=Shore power;240=Not connected | 0 indicates that there is an active input, but it is not configured under Settings → System setup.
system_battery | system_battery_voltage: | 840 | /Dc/Battery/Voltage | Battery Voltage (System) | no | V DC | Battery Voltage determined from different measurements. In order of preference: BMV-voltage (V), Multi-DC-Voltage (CV), MPPT-DC-Voltage (ScV), Charger voltage
system_battery | system_battery_current: | 841 | /Dc/Battery/Current | Battery Current (System) | no | A DC | Postive: battery begin charged. Negative: battery being discharged
system_battery | system_battery_power: | 842 | /Dc/Battery/Power | Battery Power (System) | no | W | Postive: battery begin charged. Negative: battery being discharged
system_battery | system_battery_soc: | 843 | /Dc/Battery/Soc | Battery State of Charge (System) | no | % | Best battery state of charge, determined from different measurements.
system_battery | system_battery_state: | 844 | /Dc/Battery/State | Battery state (System) | no | 0=idle;1=charging;2=discharging
system_battery | system_battery_amphours: | 845 | /Dc/Battery/ConsumedAmphours | Battery Consumed Amphours (System) | no | Ah
system_battery | system_battery_time_to_go: | 846 | /Dc/Battery/TimeToGo | Battery Time to Go (System) | no | s | Special value: 0 = charging
system_dc | system_dc_pv_power: | 850 | /Dc/Pv/Power | PV - DC-coupled power | no | W | Summation of output power of all connected Solar Chargers
system_dc | system_dc_pv_current: | 851 | /Dc/Pv/Current | PV - DC-coupled current | no | A DC | Summation of output current of all connected Solar Chargers
system_charger | system_charger_power: | 855 | /Dc/Charger/Power | Charger power | no | W
system_power | system_system_power: | 860 | /Dc/System/Power | DC System Power | no | W | Power supplied by Battery to system.
system_bus | system_bus_charge_current: | 865 | /Dc/Vebus/Current | VE.Bus charge current (System) | no | A DC | Current flowing from the Multi to the dc system. Negative: the other way around.
system_bus | system_bus_charge_power: | 866 | /Dc/Vebus/Power | VE.Bus charge power (System) | no | W | System value etc. AND: Positive: power flowing from the Multi to the dc system. Negative: the other way around.